## CSS-FD
SMARTEMP PRODUCT SELECTION CALCULATOR
Auditorium Step Diffuser [CSS-FD]
Inputs | [7 empty] | v 1.7 [06/2017]
Airflow Rate | 12 | L/s | m3/h
Maximum Permissible Total Pressure | 20 | Pa | default 20 Pa
Results
| DN100 | DN125
Sound Power Level (dB(A)) | 19.892 | 9.7172
Sound Pressure Level (dB(A)) ** | 30.892 | 19.8203
Sound Pressure Level (NC) ** | 23.8126 | < 15 | Key: | Suitable | Not Suitable | Warning
Total Pressure (Pa) | 29.8962 | 10.2767 | * | Refer to 'Notes CSS-FD' worksheet for notes and diffuser sizing
Max Selected Total Pressure (Pa) | 20 | 20 | ** | Estimated sound pressure level for seated auditorium occupant based on one diffuser per seat
Refer to 'Acoustics CSS-FD' worksheet for detailed acoustic data
| click to see product on smartair.asia | [5 empty] | Copyright © 2017 SMARTAIR DIFFUSION
Group Box 2

## CSS-FD equations (hidden)
Unit Selection
Unit Type | 1
Unit Multiplier | 1
Input Values
Airflow Rate | 12 |  | 4.9 L/s | 19 L/s
Max Pressure | 20
100 | [6 empty] | 125
Max Recommended Airflow | 9.815 | [5 empty] | Max Recommended Airflow | 16.7405
SWL (dB(A)) | 22.8529 |  | 34.92 | -63.92 |  |  | SWL (dB(A)) | 8.2902 |  | 28.94 | -63.623
Total Pressure Drop (Pa) | 29.8962 | Q-P | 8.5 | 15 |  |  | Total Pressure Drop | 10.2767 | Q-P | 16 | 18.2697
Results | DN100 | DN125
Max Selected Airflow | 12 | 12
Max Recommended Airflow | 9.815 | 16.7405
SWL (dB(A)) | 19.892 | 9.7172
SPL (db(A)) | 30.892 | 19.8203
SPL (NC) | 23.8126 | < 15
Total Pressure Drop (Pa) | 29.8962 | 10.2767
Max Permissible Pressure | 20 | 20
Acoustic
DN100 | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz
29.8962 | 20.0922 | 24.0922 | 17.786 | 14.7792 | 0 | 0
SWL (Val) | 20.0922 | 24.0922 | 17.786 | 14.7792 | < 5 | < 5
A-Weight SWL | 4.0922 | 15.0922 | 14.786 | 14.7792 | 1 | 1 | 19.892 | dBA
A-Weight | -16 | -9 | -3 | 0 | 1 | 1
SPressureL | 31.0922 | 35.0922 | 28.786 | 25.7792 | 11 | 11
A-weight SPL | 15.0922 | 26.0922 | 25.786 | 25.7792 | 12 | 12 | 30.892 | dBA
NC | 6.7508 | 21.9106 | 22.2225 | 23.8126 | 11.6 | 14.3 | 23.8126 | NC
DN125 | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz
10.2767 | 20.1546 | 12.7214 | 4.495 | 0 | -10 | -10
SWL (Val) | 20.1546 | 12.7214 | < 5 | < 5 | < 5 | < 5
A-Weight SWL | 4.1546 | 3.7214 | 1.495 | 0 | 0 | 0 | 9.7172 | dBA
A-Weight | -16 | -9 | -3 | 0 | 1 | 1
SPressureL | 31.1546 | 23.7214 | 15.495 | 11 | 1 | 1
A-weight SPL | 15.1546 | 14.7214 | 12.495 | 11 | 2 | 2 | 19.8203 | dBA
NC | 6.8325 | 8.2657 | 7.4694 | 8.59 | 1.6 | 4.6 | < 15 | NC
| 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
NC 15 | 47 | 36 | 29 | 22 | 17 | 14 | 12 | 11
NC 20 | 51 | 41 | 33 | 26 | 22 | 19 | 17 | 16
NC 25 | 54 | 45 | 38 | 31 | 27 | 24 | 22 | 21
NC 30 | 57 | 48 | 41 | 35 | 31 | 29 | 28 | 27
NC 35 | 60 | 53 | 46 | 40 | 36 | 34 | 33 | 32
NC 40 | 64 | 57 | 51 | 45 | 41 | 39 | 38 | 37

## Notes CSS-FD
SMARTEMP PRODUCT SELECTION CALCULATOR
Auditorium Step Diffuser [CSS-FD] Notes
Diffuser Sizing
| DN100 | DN125
ALL DIMENSIONS IN mm
D1 = 130
T = 100
D2 = 124
D1 = 186
T = 110
D2 = 176

## Acoustics CSS-FD
SMARTEMP PRODUCT SELECTION CALCULATOR
Auditorium Step Diffuser [CSS-FD] Acoustic Data
DN100 | [6 empty] | DN125
| 125 | 250 | 500 | 1000 | 2000 | 4000 |  | 125 | 250 | 500 | 1000 | 2000 | 4000
| 31.0922 | 35.0922 | 28.786 | 25.7792 | 11 | 11 |  | 31.1546 | 23.7214 | 15.495 | 11 | 1 | 1
DN100 | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz | DN125 | 125 Hz | 250 Hz | 500 Hz | 1000 Hz | 2000 Hz | 4000 Hz
Sound Power Level (dB) | 20.0922 | 24.0922 | 17.786 | 14.7792 | < 5 | < 5 | Sound Power Level (dB) | 20.1546 | 12.7214 | < 5 | < 5 | < 5 | < 5
Sound Power Level [dB(A)] | 19.892 | [5 empty] | Sound Power Level [dB(A)] | 9.7172
Sound Pressure Level [dB(A)] | 30.892 | [5 empty] | Sound Pressure Level [dB(A)] | 19.8203
Sound Pressure Level [NC] | 23.8126 | [5 empty] | Sound Pressure Level [NC] | < 15