## LMC-AD
SMARTEMP PRODUCT SELECTION CALCULATOR
Linear Multistream Ceiling Diffuser [LMC-AD]
Project: | <Project Name>
| Inputs | [5 empty] | Detailed Selection | [7 empty] | v 8.0 [08/2023]
| Maximum Airflow Rate | 100 | [L/s/m] | [m3/h/m] |  |  |  | Air Pattern | 2-Way | 1-Way
| VAV (turndown to) | 50 | % 10% to 100% (use 100% for CAV) |  |  |  |  | ADPI ≥ | 90% |  | default ≥ 90% |  |  |  |  | Specific Airflow Rate (heating) | 5 | L/s/m2 | 2 to 10 L/s/m2 (default 5 L/s/m2)
| Maximum Permissible Static Pressure | 30 | Pa default 30 Pa |  |  |  |  | Diffuser Location | Closed Ceiling |  | Freely Suspended
| ΔT (cooling) | -12 | K 0 K to -16 K (default -12 K) |  |  |  | Draught Rating & Heating
| Diffuser Height | 2.7 | m 2 m to 7 m (heating & cooling) |  |  |  | Diffuser Coverage = Average (Max, Min) 'C' Distance |  |  |  | see Distance section in Results
|  |  | 2 m to 11 m (cooling only) |  |  |  | OR |  | average distance = 8.8 | m
| Active Length Ratio (see diagram) | 0.5 | * 0.1 to 1.0 (default 0.5) |  |  |  |  | Manual Diffuser Coverage | 7 | m | see 'C' in diagram below
[7 empty] | OR |  | Average Specific Airflow: 5.7 | L/s/m²
[8 empty] | Specific Airflow Rate | 5 | L/s/m² | ≤ 30 L/s/m²
[9 empty] | average diffuser coverage: 10 | m
[8 empty] | Room Temperature (draught rating) | 23 | °C | 20 °C to 26 °C (default 23 °C)
[8 empty] | Low Level Return (heating) | 0 | % | 0% to 100% (default 0%)
Thermal Comfort Guide
[8 empty] | ADPI ≥ 95%; ṽ ≤ 0.20 m/s: | Premium comfort, sedentary activity, such as in auditoria.
| Spigot Size | ASNZ Sizes (DN150; DN200; DN250; DN300; DN350) | [5 empty] | ADPI ≥ 90%; ṽ ≤ 0.25 m/s: | High comfort near-sedentary activity, such as in board rooms, high end offices and libraries.
|  | DIN Sizes (DN160; DN200; DN250; DN315; DN355) | [5 empty] | ADPI ≥ 80%; ṽ ≤ 0.29 m/s: | Good comfort near sedentary activity, such as open-plan offices and meeting rooms.
[8 empty] | ADPI ≥ 70%; ṽ ≤ 0.33 m/s: | Standard comfort medium activity, such as in transient spaces, retail and lobbies.
Related Products
Smartemp LJC-AD: | for increased flow rates; optionally with thermal/electric adjustment
Smartemp LDB 12: | engineered by LTG for an ultra-slim look
Smartemp LDB 12 Clean: | engineered by LTG with SystemClean™ for minimal ceiling smudging and diffuser condensation
Smartemp LDB 50 Maxx: | engineered by LTG for high flow rates
Smartemp LMW-AD: | for a wall-mounted solution
Results | SMARTEMP LMC-AD |  | 1 Slot | 2 Slots | 3 Slots | 4 Slots | 5 Slots | 6 Slots | 7 Slots | 8 Slots | Key: | Suitable | Not Suitable | Warning
Dimensions * | Width Flangeless Face | [mm] | 31 | 59 | 87 | 115 | 143 | 171 | 199 | 227
| Width Flanged Face | [mm] | 48 | 76 | 104 | 132 | 160 | 188 | 216 | 244
| Width of Diffuser Throat | [mm] | 27 | 55 | 83 | 111 | 139 | 167 | 195 | 223
Airflow | Selected Airflow Rate | [L/s/m] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Airflow @ Max Static Pressure | [L/s/m] | 34 | 71 | 109 | 144 | 186 | 229 | 262 | 308
| Min Selected Airflow | [L/s/m] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
| Min Permissible Airflow @ -12 K | [L/s/m] | 7.6 | 16 | 24.2 | 32.3 | 40.7 | 49.4 | 57.4 | 65.8
| Min % Turndown to |  | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50%
| Min Permissible % Turndown to |  | 8% | 16% | 24% | 32% | 41% | 49% | 57% | 66%
Pressure | Static Pressure @ 100% Airflow | [Pa] | 266.1 | 60 | 25.4 | 14.5 | 8.7 | 5.7 | < 4.5 | < 4.5
| Total Pressure @ 100% Airflow | [Pa] | 272.3 | 66.2 | 31.6 | 20.7 | 14.9 | 11.9 | 10.6 | 9.4
| Max Selected Total Pressure | [Pa] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Acoustic | Sound Power Level | [dB(A)/m] | 48.4 | 41.2 | 34.4 | 27.9 | 22.7 | 16.4 | < 15 | < 15
| Sound Pressure Level ^ | [NC/m] | 33.4 | 26.2 | 19.4 | 12.9 | < 10 | < 10 | < 10 | < 10
Cooling & Heating | Air Direction Setting ** | [9 empty] | - Direction setting for balanced cooling and heating performance | bar: 8% to 66%
| Centre Zone: Heating ΔT Max | [K] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
| Perimeter Zone: Heating ΔT Max | [K] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | Heating ΔT valid at 100% airflow rate
Max Heating | ΔT with Vertical Discharge | [K] | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | - Direction setting 'E' (90° Discharge)
Recommended Distances & Layout ** | Max Coverage Centre Zones (Cmax) | [m] | 17.9 | 14.9 | 14.1 | 13.6 | 13.4 | 13.2 | 13.1 | 13
| Max Coverage Perimeter Zones (Cmax) | [m] | 17.9 | 14.4 | 13.2 | 12.7 | 12.3 | 12.1 | 12 | 11.9 | Rows 60 - 62 Warning: Threat of draught when Cmin > Cmax. Consider: increasing 'Active Length Ratio', increasing 'Turndown To', or decreasing 'ADPI'
| Min Coverage (Cmin) | [m] | 16.8 | 6.5 | 5.4 | 5 | 4.8 | 4.7 | 4.6 | 4.5
| Min Diffuser Height | [m] | 2.5 | 2.5 | 2.6 | 2.6 | 2.7 | 2.7 | 2.8 | 2.8
Comfort | Mean Room Air Velocity [m/s] | [m/s] | 0.2 | 0.17 | 0.16 | 0.15 | 0.15 | 0.14 | 0.14 | 0.14 | Note: Comfort criteria valid for diffuser spacing of 8.8 m & room temperature of 23 °C (see cells L18:L21 & L23)
| Mean Draught Rating (DR) |  | 20.5% | 16.3% | 14.8% | 14.1% | 13.6% | 13.3% | 13.1% | 12.9%
| Mean PPD |  | 10.2% | 8.4% | 7.8% | 7.5% | 7.3% | 7.2% | 7.1% | 7.1% | * | Refer to 'Dimensions LMC-AD' worksheet for details
| ¦PMV¦ |  | < 0.5 | < 0.4 | < 0.4 | < 0.4 | < 0.3 | < 0.3 | < 0.3 | < 0.3 | ** | Refer to 'Notes LMC-AD' worksheet for definitions and details
| Satisfies PPD Category (ISO7730) | [9 empty] | ^ | Based on 10 dB room absorption | bar: 8% to 66%
| Nominal Spigot Size /m |  | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200
Product Selection & Code Generator
| Select model to create product code |  | 1 slot | 2 slots | 3 slots | 4 slots | 5 slots | 6 slots | 7 slots | 8 slots
| Supply/Return |  | 16%: supply: adjustable direction; 32%: return air
| Nominal Length |  | 16%: 1195 mm* (face); 32%: 1200 mm (neck); 49%: custom^ (face) ≤ 1500 mm
| Air Pattern Setting |  | 16%: 2-way blow selected | - see Cell K8
| Air Direction Setting |  | recommended | A* (0 to -15°) |  | B (0 to -30°) | C (≈ -45°) | D (≈ -60°) | E (vertical) | custom
| Side Profile |  | 16%: with side flanges*; 32%: flangeless
| Diffuser Ends |  | 8%: 2 end flanges *; 24%: 1 end flange & 1 pair joining strips; 49%: 1 pair joining strips; 66%: no end flanges
| Fixing |  | 8%: without accessories/by others *; 32%: expansion bracket; 49%: mounting frame for plasterboard
| Profile Colour |  | 16%: RAL9003* (signal white); 32%: RAL9005 (jet black); 49%: other ^ | ^ contact Smartair Diffusion for custom lengths and colours
| Barrel Colour |  | 16%: black*; 24%: white | * indicates standard/default option
| Connection Box |  | 8%: No connection box *; 24%: uninsulated connection box; 49%: internally insulated connection box
|  |  | 32%: clipped to diffuser throat; 49%: screwed to diffuser throat | options only available with connection box
| Product Code |  | 8%: SMARTEMP LMC-AD-F1195-2-2A-SF-E2-MFP-RAL9003-B-K0; 57%: more detailed options available in the LMC-AD product brochure
go to 'LMC-AD Selection Print Summary' for a printable summary of the selection
|  |  | 24%: click here to see product on smartair.asia |  |  | Copyright © 2023 SMARTAIR DIFFUSION
Group Box 28
Group Box 35
Group Box 41
Group Box 38
Group Box 49
Group Box 53
Group Box 72
Group Box 17
Group Box 121
Group Box 130
Group Box 134
Group Box 24
Group Box 924
Group Box 127

## LMC-ADequations (hidden)
Units
Units | 1 | [L/s/m] | L/s/m
Units Multiplier | 1 | L/s/m² | L/s
Input Values
Airflow Rate | 100
VAV | 50
Max Total Pressure | 30
dT(cooling) | -12
Room Height | 2.7
Length Ratio | 0.5
Air Pattern | 2
Specific airflow | 5
ADPI | 0.9
LRA | 0
Ceiling | 1
Room Temperature | 23 | C
Manual C distance | 7 | m
distance input type | 1
Input Validation
Airflow Rate | 100
VAV | 0.5
Airflow Rate (TD) | 50
Max Total Pressure | 30
dT(cooling) | 12
Room Height | 2.7
Length Ratio | 0.5
Air Pattern | 2
ADPI | 90%
Local Velocity | 0.25
LRA | 100%
Ceiling Type | 0 | Closed
Ceiling Type Heating | 1
Ceiling Type Hmin | 1
Draft Rating | 27.74%
Global Distance | 8.7941
Spigot Selection | 1 |  |  | AU/NZ |  |  |  | DIN |  | v
Spigot size | 200 | mm | 1 | 150 | 0.017671 | 0 | 1 | 160 | 0.020106 | 0
Spigot Area | 0.031416 | m2 | 2 | 200 | 0.031416 | 3.1831 | 2 | 200 | 0.031416 | 3.1831
Spigot Velocity | 3.1831 | m/s | 3 | 250 | 0.049087 | 2.0372 | 3 | 250 | 0.049087 | 2.0372
|  |  | 4 | 300 | 0.070686 | 1.4147 | 4 | 315 | 0.077931 | 1.2832
|  |  | 5 | 350 | 0.096211 | 1.0394 | 5 | 355 | 0.09898 | 1.0103
|  |  | 2 | 200 | 0.031416 | 3.1831 | 2 | 200 | 0.031416 | 3.1831
Cmin Ceiling Factor | 1
Cmax Ceiling Factor | 1
V_turndown | 50 |  | v_td=fr*vav
Diffuser Airflow for Neck Length | 116.3 | 1.163 | 1163
Hmin
Hmin 2WAY | 2.6012 |  | 0.04282 | 2.173
Hmin 1WAY | 2.7786
Hmin Select | 2.6012
Hmin DT factor | 1.05
ADPI
Hmin | 95% | 2.7012
| 90% | 2.6012
| 80% | 2.5012
| 70% | 2.4012
Cmin | 2-WAY |  |  |  | 1-WAY |  |  |  |  | Q' to v'
|  |  | Target Q'' |  |  |  | Target Q'' |  |  |  | 2-Way |  | 1-Way |  | Selection
H | ax | ^b | Q'' |  | ax | ^b | Q'' |  |  |  | ax | ^b | ax | ^b | ax | ^b
2.7 | 4510 | 2.2693 | 194.0536 |  | 2886 | 2.152 | 146.1044 |  |  | 2.7 | 0.02455 | 0.4405 | 0.02466 | 0.4647 | 0.02455 | 0.4405
4 | 3884 | 2.2426 | 173.4201 |  | 2651 | 2.175 | 129.9958 |  |  | 4 | 0.0251 | 0.4458 | 0.02669 | 0.4597 | 0.0251 | 0.4458
10.0001 | 3435 | 2.2754 | 146.5546 |  | 2317 | 2.194 | 110.664 |  |  | 10.0001 | 0.02797 | 0.4391 | 0.02927 | 0.4557 | 0.02797 | 0.4391
| Ax | ^b |  |  | Ax | ^b
2.7 | 235.858 | -0.20897 | 191.6493 | W/m2 | 176.5945 | -0.20573 | 143.9573 | W/m2
Q" allowed | 191.6493
v' for Vmax | 15.9708 | L/s/m2
v' for Vmin | 19.9708 | L/s/m2
v'' + correction factor | 4
Active Length Factor | 0.90063
Cmax
ADPI | for Vmax | for Vmin |  | Hfactor @ Vmax | Hfactor @ Vmin
95% | 1.91 | 2.54 |  | 5.317 | 4.4309
90% | 1.5 | 2 |  | 6 | 5
80% | 1 | 1.32 |  | 7.3659 | 6.1383
70% | 0.7 | 0.94 |  | 8.7318 | 7.2765 | [46 empty] | Q | SWL | P | A | B
at Vmax | 1.5 |  | at adpi | 6 | [47 empty] | 130 | 0 | 5.3438 | 15.324 | -2.6401
at Vmin | 2 |  |  | 5 | [47 empty] | 210 | 0 | 13.9446
[52 empty] | 280 | 0 | 24.7903
Cmax-Centre Zone
ADPI | for Vmax | for Vmin |  | Hfactor @ Vmax | Hfactor @ Vmin
95% | 1.5 | 2 |  | 5.317 | 4.4309
90% | 1.2152 | 1.6165 |  | 6 | 5
80% | 0.80587 | 1.0763 |  | 7.3659 | 6.1383
70% | 0.7 | 0.94 |  | 8.7318 | 7.2765
at Vmax | 1.2152 |  | at adpi | 6
at Vmin | 1.6165 |  |  | 5 | [47 empty] | 330 | 0 | 34.4345
Heating
Height | Slope
2 | 1.0112 | [50 empty] | SWL | 15.0011
2.7 | 0.66726
3 | 0.54867
4 | 0.27434
5 | 0.088496
2.7 | 0.65159
Air Pattern Settings |  | 2 WAY | 1 WAY | Selection
1 | 3.15 | A | AB | A
2 | 4.2 | B | AC | B
3 |  | C | BC | C
Exit width per row | 0.013
1Slot | [6 empty] | 2Slot | [6 empty] | 3Slot | [5 empty] | 4Slot | [5 empty] | 5Slot | [5 empty] | 6Slot | [5 empty] | 7Slot | [5 empty] | 8Slot
Slots | 1 | [5 empty] | Slots | 2 | [5 empty] | Slots | 3 |  |  |  |  | Slots | 4 |  |  |  |  | Slots | 5 |  |  |  |  | Slots | 6 |  |  |  |  | Slots | 7 |  |  |  |  | Slots | 8
data.Flowrate | 35 | L/s/m |  |  |  |  | data.Flowrate | 74 | L/s/m |  |  |  |  | data.Flowrate | 112 | L/s/m |  |  |  | data.Flowrate | 149 | L/s/m |  |  |  | data.Flowrate | 188 | L/s/m |  |  |  | data.Flowrate | 228 | L/s/m |  |  |  | data.Flowrate | 265 | L/s/m |  |  |  | data.Flowrate | 304 | L/s/m
data.Pressure | 35 | Pa |  |  |  |  | data.Pressure | 35 | Pa |  |  |  |  | data.Pressure | 35 | Pa |  |  |  | data.Pressure | 35 | Pa |  |  |  | data.Pressure | 35 | Pa |  |  |  | data.Pressure | 35 | Pa |  |  |  | data.Pressure | 35 | Pa |  |  |  | data.Pressure | 35 | Pa
data.Static Pressure | 32.5973 | Pa |  |  |  |  | data.Static Pressure | 32.8784 | [5 empty] | data.Static Pressure | 31.8114 |  |  |  |  | data.Static Pressure | 32.2785 |  |  |  |  | data.Static Pressure | 30.6673 |  |  |  |  | data.Static Pressure | 29.7573 |  |  |  |  | data.Static Pressure | 30.6096 |  |  |  |  | data.Static Pressure | 29.2222
Static Pressure @ Flowrate | 266.1005 | [5 empty] | Static Pressure @ Flowrate | 60.0409 | [5 empty] | Static Pressure @ Flowrate | 25.3598 |  |  |  |  | Static Pressure @ Flowrate | 14.5392 |  |  |  |  | Static Pressure @ Flowrate | 8.6768 |  |  |  |  | Static Pressure @ Flowrate | 5.7243 |  |  |  |  | Static Pressure @ Flowrate | 4.3588 |  |  |  |  | Static Pressure @ Flowrate | 3.162
Total Pressure @Flowrate | 272.3064 | Pa |  |  |  |  | Total Pressure @Flowrate | 66.2469 | Pa |  |  |  |  | Total Pressure @Flowrate | 31.5658 | Pa |  |  |  | Total Pressure @Flowrate | 20.7451 | Pa |  |  |  | Total Pressure @Flowrate | 14.8827 | Pa |  |  |  | Total Pressure @Flowrate | 11.9302 | Pa |  |  |  | Total Pressure @Flowrate | 10.5647 | Pa |  |  |  | Total Pressure @Flowrate | 9.368 | Pa
Flowrate @MaxP | 33.5767 | [5 empty] | Flowrate @MaxP | 70.6866 | [5 empty] | Flowrate @MaxP | 108.7646 |  |  |  |  | Flowrate @MaxP | 143.645 |  |  |  |  | Flowrate @MaxP | 185.9433 |  |  |  |  | Flowrate @MaxP | 228.9278 |  |  |  |  | Flowrate @MaxP | 262.348 |  |  |  |  | Flowrate @MaxP | 308.019
V_min | 7.5777 | [5 empty] | V_min | 16.0215 | [5 empty] | V_min | 24.2487 |  |  |  |  | V_min | 32.2594 |  |  |  |  | V_min | 40.7032 |  |  |  |  | V_min | 49.3634 |  |  |  |  | V_min | 57.3742 |  |  |  |  | V_min | 65.8179
Min % TD to | 7.578% | [5 empty] | Min % TD to | 16.02% | [5 empty] | Min % TD to | 24.25% |  |  |  |  | Min % TD to | 32.26% |  |  |  |  | Min % TD to | 40.7% |  |  |  |  | Min % TD to | 49.36% |  |  |  |  | Min % TD to | 57.37% |  |  |  |  | Min % TD to | 65.82%
SWL - Static Pressure Coefficients | [6 empty] | SWL - Static Pressure Coefficients | [6 empty] | SWL - Static Pressure Coefficients | [5 empty] | SWL - Static Pressure Coefficients | [5 empty] | SWL - Static Pressure Coefficients | [5 empty] | SWL - Static Pressure Coefficients | [5 empty] | SWL - Static Pressure Coefficients | [5 empty] | SWL - Static Pressure Coefficients
A | 9.1038 | [5 empty] | A | 10.92 | [5 empty] | A | 12.23 |  |  |  |  | A | 12.575 |  |  |  |  | A | 12.667 |  |  |  |  | A | 14.312 |  |  |  |  | A | 14.312 |  |  |  |  | A | 14.312
B | -2.4592 | [5 empty] | B | -3.4754 | [5 empty] | B | -5.1697 |  |  |  |  | B | -5.7516 |  |  |  |  | B | -4.6794 |  |  |  |  | B | -8.6166 |  |  |  |  | B | -7.947 |  |  |  |  | B | -7.367
SWL | 48.3753 | [5 empty] | SWL | 41.2423 | [5 empty] | SWL | 34.3719 |  |  |  |  | SWL | 27.9098 |  |  |  |  | SWL | 22.6896 |  |  |  |  | SWL | 16.3539 |  |  |  |  | SWL | 13.123 |  |  |  |  | SWL | 9.1092
SPL | 33.3753 |  | SWL-15 |  |  |  | SPL | 26.2423 |  | SWL-15 |  |  |  | SPL | 19.3719 |  | SWL-15 |  |  | SPL | 12.9098 |  | SWL-15 |  |  | SPL | 7.6896 |  | SWL-15 |  |  | SPL | 1.3539 |  | SWL-15 |  |  | SPL | -1.877 |  | SWL-15 |  |  | SPL | -5.8908 |  | SWL-15
Hmin
Hmin Factor | 0.9 | [5 empty] | Hmin Factor | 0.92 | [5 empty] | Hmin Factor | 0.94 |  |  |  |  | Hmin Factor | 0.96 |  |  |  |  | Hmin Factor | 0.98 |  |  |  |  | Hmin Factor | 1 |  |  |  |  | Hmin Factor | 1.02 |  |  |  |  | Hmin Factor | 1.04
Min Diffuser Height (m) | 2.4581 | [5 empty] | Min Diffuser Height (m) | 2.5128 | [5 empty] | Min Diffuser Height (m) | 2.5674 |  |  |  |  | Min Diffuser Height (m) | 2.622 |  |  |  |  | Min Diffuser Height (m) | 2.6766 |  |  |  |  | Min Diffuser Height (m) | 2.7313 |  |  |  |  | Min Diffuser Height (m) | 2.7859 |  |  |  |  | Min Diffuser Height (m) | 2.8405
Air Direction Setting | [6 empty] | Air Direction Setting | [6 empty] | Air Direction Setting | [5 empty] | Air Direction Setting | [5 empty] | Air Direction Setting | [5 empty] | Air Direction Setting | [5 empty] | Air Direction Setting | [5 empty] | Air Direction Setting
Band Delta H | -0.36872 | [5 empty] | Band Delta H | -0.29498 | [5 empty] | Band Delta H | -0.22123 |  |  |  |  | Band Delta H | -0.14749 |  |  |  |  | Band Delta H | -0.073744 |  |  |  |  | Band Delta H | 0 |  |  |  |  | Band Delta H | 0.073744 |  |  |  |  | Band Delta H | 0.14749
Direction Setting Table | H | [5 empty] | Direction Setting Table | H | [5 empty] | Direction Setting Table | H |  |  |  |  | Direction Setting Table | H |  |  |  |  | Direction Setting Table | H |  |  |  |  | Direction Setting Table | H |  |  |  |  | Direction Setting Table | H |  |  |  |  | Direction Setting Table | H
1 | 2.7813 | [5 empty] | 1 | 2.855 | [5 empty] | 1 | 2.9288 |  |  |  |  | 1 | 3.0025 |  |  |  |  | 1 | 3.0763 |  |  |  |  | 1 | 3.15 |  |  |  |  | 1 | 3.2237 |  |  |  |  | 1 | 3.2975
2 | 3.8313 | [5 empty] | 2 | 3.905 | [5 empty] | 2 | 3.9788 |  |  |  |  | 2 | 4.0525 |  |  |  |  | 2 | 4.1263 |  |  |  |  | 2 | 4.2 |  |  |  |  | 2 | 4.2737 |  |  |  |  | 2 | 4.3475
3 | [6 empty] | 3 | [6 empty] | 3 | [5 empty] | 3 | [5 empty] | 3 | [5 empty] | 3 | [5 empty] | 3 | [5 empty] | 3
Selection | A | [5 empty] | Selection | A | [5 empty] | Selection | A |  |  |  |  | Selection | A |  |  |  |  | Selection | A |  |  |  |  | Selection | A |  |  |  |  | Selection | A |  |  |  |  | Selection | A
Distance Selection | [6 empty] | Distance Selection | [6 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection
Vmax | 35 | [5 empty] | Vmax | 74 | [5 empty] | Vmax | 112 |  |  |  |  | Vmax | 149 |  |  |  |  | Vmax | 188 |  |  |  |  | Vmax | 228 |  |  |  |  | Vmax | 265 |  |  |  |  | Vmax | 304
Vmin | 10.5 | [5 empty] | Vmin | 22.2 | [5 empty] | Vmin | 33.6 |  |  |  |  | Vmin | 44.7 |  |  |  |  | Vmin | 56.4 |  |  |  |  | Vmin | 68.4 |  |  |  |  | Vmin | 79.5 |  |  |  |  | Vmin | 91.2
Cmin | [6 empty] | Cmin | [6 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin
at V (L/s/m^2) | 5.3585 | [5 empty] | at V (L/s/m^2) | 13.9631 | [5 empty] | at V (L/s/m^2) | 16.583 |  |  |  |  | at V (L/s/m^2) | 17.85 |  |  |  |  | at V (L/s/m^2) | 18.6456 |  |  |  |  | at V (L/s/m^2) | 19.1788 |  |  |  |  | at V (L/s/m^2) | 19.5287 |  |  |  |  | at V (L/s/m^2) | 19.8054
Cmin | 16.8073 | [5 empty] | Cmin | 6.4501 | [5 empty] | Cmin | 5.431 |  |  |  |  | Cmin | 5.0455 |  |  |  |  | Cmin | 4.8302 |  |  |  |  | Cmin | 4.6959 |  |  |  |  | Cmin | 4.6118 |  |  |  |  | Cmin | 4.5474
Cmax Perimeter | [6 empty] | Cmax Perimeter | [6 empty] | Cmax | [5 empty] | Cmax | [5 empty] | Cmax | [5 empty] | Cmax | [5 empty] | Cmax | [5 empty] | Cmax
v' @ V | 1.1939 | [5 empty] | v' @ V | 1.7317 | [5 empty] | v' @ V | 1.8954 |  |  |  |  | v' @ V | 1.9746 |  |  |  |  | v' @ V | 2.0243 |  |  |  |  | v' @ V | 2.0576 |  |  |  |  | v' @ V | 2.0795 |  |  |  |  | v' @ V | 2.0968
h factor @ V | 6.6122 | [5 empty] | h factor @ V | 5.5367 | [5 empty] | h factor @ V | 5.2092 |  |  |  |  | h factor @ V | 5.0508 |  |  |  |  | h factor @ V | 4.9514 |  |  |  |  | h factor @ V | 4.8847 |  |  |  |  | h factor @ V | 4.841 |  |  |  |  | h factor @ V | 4.8064
Cmax | 20.9402 | [5 empty] | Cmax | 14.437 | [5 empty] | Cmax | 13.1898 |  |  |  |  | Cmax | 12.6608 |  |  |  |  | Cmax | 12.3498 |  |  |  |  | Cmax | 12.1498 |  |  |  |  | Cmax | 12.022 |  |  |  |  | Cmax | 11.9229
Cmax room height | 17.8531 | [5 empty] | Cmax room height | 14.949 |  | ROOM TO INCLUDE FREE CEILING factor?? |  |  |  | Cmax room height | 14.0648 |  |  |  |  | Cmax room height | 13.6372 |  |  |  |  | Cmax room height | 13.3687 |  |  |  |  | Cmax room height | 13.1887 |  |  |  |  | Cmax room height | 13.0706 |  |  |  |  | Cmax room height | 12.9773
Cmax Min of above | 17.8531 | final selection |  |  |  |  | Cmax Min of above | 14.437 | final selection |  |  |  |  | Cmax Min of above | 13.1898 | final selection |  |  |  | Cmax Min of above | 12.6608 | final selection |  |  |  | Cmax Min of above | 12.3498 | final selection |  |  |  | Cmax Min of above | 12.1498 | final selection |  |  |  | Cmax Min of above | 12.022 | final selection |  |  |  | Cmax Min of above | 11.9229 | final selection
Cmax centre zone | [6 empty] | Cmax centre zone | [6 empty] | Cmax centre zone | [5 empty] | Cmax centre zone | [5 empty] | Cmax centre zone | [5 empty] | Cmax centre zone | [5 empty] | Cmax centre zone | [5 empty] | Cmax centre zone
v' @ V | 0.96954 | [5 empty] | v' @ V | 1.4012 | [5 empty] | v' @ V | 1.5326 |  |  |  |  | v' @ V | 1.5961 |  |  |  |  | v' @ V | 1.6361 |  |  |  |  | v' @ V | 1.6628 |  |  |  |  | v' @ V | 1.6804 |  |  |  |  | v' @ V | 1.6942
h factor @ V | 6.6122 | [5 empty] | h factor @ V | 5.5367 | [5 empty] | h factor @ V | 5.2092 |  |  |  |  | h factor @ V | 5.0508 |  |  |  |  | h factor @ V | 4.9514 |  |  |  |  | h factor @ V | 4.8847 |  |  |  |  | h factor @ V | 4.841 |  |  |  |  | h factor @ V | 4.8064
Cmax | 25.7855 | [5 empty] | Cmax | 17.8423 | [5 empty] | Cmax | 16.3122 |  |  |  |  | Cmax | 15.6627 |  |  |  |  | Cmax | 15.2806 |  |  |  |  | Cmax | 15.0348 |  |  |  |  | Cmax | 14.8778 |  |  |  |  | Cmax | 14.7559
Cmax room height | 17.8531 | [5 empty] | Cmax room height | 14.949 | [5 empty] | Cmax room height | 14.0648 |  |  |  |  | Cmax room height | 13.6372 |  |  |  |  | Cmax room height | 13.3687 |  |  |  |  | Cmax room height | 13.1887 |  |  |  |  | Cmax room height | 13.0706 |  |  |  |  | Cmax room height | 12.9773
Cmax Min of above | 17.8531 | final selection |  |  |  |  | Cmax Min of above | 14.949 | final selection |  |  |  |  | Cmax Min of above | 14.0648 | final selection |  |  |  | Cmax Min of above | 13.6372 | final selection |  |  |  | Cmax Min of above | 13.3687 | final selection |  |  |  | Cmax Min of above | 13.1887 | final selection |  |  |  | Cmax Min of above | 13.0706 | final selection |  |  |  | Cmax Min of above | 12.9773 | final selection |  |  |  | Cmax Min of above | 0
Comfort | [6 empty] | Comfort | [6 empty] | Comfort | [5 empty] | Comfort | [5 empty] | Comfort | [5 empty] | Comfort | [5 empty] | Comfort | [5 empty] | Comfort
global avg dist | [6 empty] | global avg dist | [6 empty] | global avg dist | [5 empty] | global avg dist | [5 empty] | global avg dist | [5 empty] | global avg dist | [5 empty] | global avg dist | [5 empty] | global avg dist
diffuser dist from spec. afr | [6 empty] | diffuser dist from spec. afr | [6 empty] | diffuser dist from spec. afr | [5 empty] | diffuser dist from spec. afr | [5 empty] | diffuser dist from spec. afr | [5 empty] | diffuser dist from spec. afr | [5 empty] | diffuser dist from spec. afr | [5 empty] | diffuser dist from spec. afr
diffuser dist selected | [6 empty] | diffuser dist selected | [6 empty] | diffuser dist selected | [5 empty] | diffuser dist selected | [5 empty] | diffuser dist selected | [5 empty] | diffuser dist selected | [5 empty] | diffuser dist selected | [5 empty] | diffuser dist selected
Area | [6 empty] | Area | [6 empty] | Area | [5 empty] | Area | [5 empty] | Area | [5 empty] | Area | [5 empty] | Area | [5 empty] | Area
v" | 5.6856 | L/s/m2 |  |  |  |  | v" | 5.6856 | L/s/m3 |  |  |  |  | v" | 5.6856 | L/s/m4 |  |  |  | v" | 5.6856 | L/s/m5 |  |  |  | v" | 5.6856 | L/s/m6 |  |  |  | v" | 5.6856 | L/s/m7 |  |  |  | v" | 5.6856 | L/s/m8 |  |  |  | v" | 5.6856 | L/s/m9
velocity adjustment |  |  | for total area |  |  |  | velocity adjustment |  |  | for total area |  |  |  | velocity adjustment |  |  | for total area |  |  | velocity adjustment |  |  | for total area |  |  | velocity adjustment |  |  | for total area |  |  | velocity adjustment |  |  | for total area |  |  | velocity adjustment |  |  | for total area |  |  | velocity adjustment |  |  | for total area
Q'' | 68.2274 | W/m2 |  |  |  |  | Q'' | 68.2274 | W/m3 |  |  |  |  | Q'' | 68.2274 | W/m4 |  |  |  | Q'' | 68.2274 | W/m5 |  |  |  | Q'' | 68.2274 | W/m6 |  |  |  | Q'' | 68.2274 | W/m7 |  |  |  | Q'' | 68.2274 | W/m8 |  |  |  | Q'' | 68.2274 | W/m9
v'' correction factor | -3.7711 | [5 empty] | v'' correction factor | -0.71345 | [5 empty] | v'' correction factor | 0.21756 |  |  |  |  | v'' correction factor | 0.66777 |  |  |  |  | v'' correction factor | 0.95048 |  |  |  |  | v'' correction factor | 1.14 |  |  |  |  | v'' correction factor | 1.2643 |  |  |  |  | v'' correction factor | 1.3626
v'' (adjusted) | 9.4567 | [5 empty] | v'' (adjusted) | 6.3991 | [5 empty] | v'' (adjusted) | 5.4681 |  |  |  |  | v'' (adjusted) | 5.0178 |  |  |  |  | v'' (adjusted) | 4.7351 |  |  |  |  | v'' (adjusted) | 4.5456 |  |  |  |  | v'' (adjusted) | 4.4213 |  |  |  |  | v'' (adjusted) | 4.323
Q'' (adjusted) | 113.4802 |  | no air density for max to mean velocity |  |  |  | Q'' (adjusted) | 76.7887 |  | no air density for max to mean velocity |  |  |  | Q'' (adjusted) | 65.6166 |  | no air density for max to mean velocity |  |  | Q'' (adjusted) | 60.2141 |  | no air density for max to mean velocity |  |  | Q'' (adjusted) | 56.8216 |  | no air density for max to mean velocity |  |  | Q'' (adjusted) | 54.5477 |  | no air density for max to mean velocity |  |  | Q'' (adjusted) | 53.0555 |  | no air density for max to mean velocity |  |  | Q'' (adjusted) | 51.8759 |  | no air density for max to mean velocity
2.7 | 0.19735 | [5 empty] | 2.7 | 0.16616 | [5 empty] | 2.7 | 0.15504 |  |  |  |  | 2.7 | 0.14928 |  |  |  |  | 2.7 | 0.14552 |  |  |  |  | 2.7 | 0.14292 |  |  |  |  | 2.7 | 0.14119 |  |  |  |  | 2.7 | 0.1398
4 | 0.2069 | [5 empty] | 4 | 0.17384 | [5 empty] | 4 | 0.16207 |  |  |  |  | 4 | 0.15598 |  |  |  |  | 4 | 0.152 |  |  |  |  | 4 | 0.14925 |  |  |  |  | 4 | 0.14742 |  |  |  |  | 4 | 0.14595
10 | 0.22336 | [5 empty] | 10 | 0.18816 | [5 empty] | 10 | 0.17561 |  |  |  |  | 10 | 0.16911 |  |  |  |  | 10 | 0.16485 |  |  |  |  | 10 | 0.16192 |  |  |  |  | 10 | 0.15996 |  |  |  |  | 10 | 0.15839
For Room Height | Ax | B |  |  |  |  | For Room Height | Ax | B |  |  |  |  | For Room Height | Ax | B |  |  |  | For Room Height | Ax | B |  |  |  | For Room Height | Ax | B |  |  |  | For Room Height | Ax | B |  |  |  | For Room Height | Ax | B |  |  |  | For Room Height | Ax | B
| 0.18082 | 0.092603 | [5 empty] | 0.15196 | 0.093453 | [5 empty] | 0.14168 | 0.093794 |  |  |  |  | 0.13637 | 0.093981 |  |  |  |  | 0.13289 | 0.094107 |  |  |  |  | 0.1305 | 0.094196 |  |  |  |  | 0.1289 | 0.094257 |  |  |  |  | 0.12761 | 0.094305
Velocity | 0.19824 | m/s |  |  |  |  | Velocity | 0.16674 | m/s |  |  |  |  | Velocity | 0.15552 | m/s |  |  |  | Velocity | 0.14971 | m/s |  |  |  | Velocity | 0.14591 | m/s |  |  |  | Velocity | 0.1433 | m/s |  |  |  | Velocity | 0.14155 | m/s |  |  |  | Velocity | 0.14014 | m/s
Draught Rating | 20.46% | [5 empty] | Draught Rating | 16.29% | [5 empty] | Draught Rating | 14.85% |  |  |  |  | Draught Rating | 14.11% |  |  |  |  | Draught Rating | 13.63% |  |  |  |  | Draught Rating | 13.3% |  |  |  |  | Draught Rating | 13.08% |  |  |  |  | Draught Rating | 12.9%
PPD | 10.21% | [5 empty] | PPD | 8.398% | [5 empty] | PPD | 7.813% |  |  |  |  | PPD | 7.522% |  |  |  |  | PPD | 7.335% |  |  |  |  | PPD | 7.208% |  |  |  |  | PPD | 7.124% |  |  |  |  | PPD | 7.057%
PPD Class | C | [5 empty] | PPD Class | B | [5 empty] | PPD Class | B |  |  |  |  | PPD Class | B |  |  |  |  | PPD Class | B |  |  |  |  | PPD Class | B |  |  |  |  | PPD Class | B |  |  |  |  | PPD Class | B
PMV | 0.52034 | [5 empty] | PMV | 0.41715 | [5 empty] | PMV | 0.37518 |  |  |  |  | PMV | 0.35208 |  |  |  |  | PMV | 0.3364 |  |  |  |  | PMV | 0.32532 |  |  |  |  | PMV | 0.31777 |  |  |  |  | PMV | 0.31164
PMV | 0.5 | [5 empty] | PMV | 0.4 | [5 empty] | PMV | 0.4 |  |  |  |  | PMV | 0.4 |  |  |  |  | PMV | 0.3 |  |  |  |  | PMV | 0.3 |  |  |  |  | PMV | 0.3 |  |  |  |  | PMV | 0.3
ADPI ACTUAL
ADPI Actual Cmin | [6 empty] | ADPI Actual | [6 empty] | ADPI Actual | [5 empty] | ADPI Actual | [5 empty] | ADPI Actual | [5 empty] | ADPI Actual | [5 empty] | ADPI Actual | [5 empty] | ADPI Actual
Q'' (adjusted) for active length | 226.9604 | [5 empty] | Q'' (adjusted) for active length | 153.5774 | [5 empty] | Q'' (adjusted) for active length | 131.2332 |  |  |  |  | Q'' (adjusted) for active length | 120.4281 |  |  |  |  | Q'' (adjusted) for active length | 113.6431 |  |  |  |  | Q'' (adjusted) for active length | 109.0954 |  |  |  |  | Q'' (adjusted) for active length | 106.111 |  |  |  |  | Q'' (adjusted) for active length | 103.7517
2.7 | 0.26782 |  | (fix rounding errors) |  |  |  | 2.7 | 0.22549 | [5 empty] | 2.7 | 0.2104 |  |  |  |  | 2.7 | 0.20259 |  |  |  |  | 2.7 | 0.19748 |  |  |  |  | 2.7 | 0.19396 |  |  |  |  | 2.7 | 0.1916 |  |  |  |  | 2.7 | 0.18971
4 | 0.28181 | [5 empty] | 4 | 0.23678 | [5 empty] | 4 | 0.22075 |  |  |  |  | 4 | 0.21245 |  |  |  |  | 4 | 0.20703 |  |  |  |  | 4 | 0.2033 |  |  |  |  | 4 | 0.2008 |  |  |  |  | 4 | 0.19879
10 | 0.30282 | [5 empty] | 10 | 0.2551 | [5 empty] | 10 | 0.23808 |  |  |  |  | 10 | 0.22927 |  |  |  |  | 10 | 0.2235 |  |  |  |  | 10 | 0.21953 |  |  |  |  | 10 | 0.21687 |  |  |  |  | 10 | 0.21474
For Room Height | Ax | B |  |  |  |  | For Room Height | Ax | B |  |  |  |  | For Room Height | Ax | B |  |  |  | For Room Height | Ax | B |  |  |  | For Room Height | Ax | B |  |  |  | For Room Height | Ax | B |  |  |  | For Room Height | Ax | B |  |  |  | For Room Height | Ax | B
| 0.24618 | 0.091096 | [5 empty] | 0.20689 | 0.091945 | [5 empty] | 0.1929 | 0.092287 |  |  |  |  | 0.18566 | 0.092474 |  |  |  |  | 0.18093 | 0.0926 |  |  |  |  | 0.17767 | 0.092689 |  |  |  |  | 0.17549 | 0.092749 |  |  |  |  | 0.17374 | 0.092798
Velocity | 0.27 | m/s |  |  |  |  | Velocity | 0.23 | m/s |  |  |  |  | Velocity | 0.21 | m/s |  |  |  | Velocity | 0.2 | m/s |  |  |  | Velocity | 0.2 | m/s |  |  |  | Velocity | 0.19 | m/s |  |  |  | Velocity | 0.19 | m/s |  |  |  | Velocity | 0.19 | m/s
ADPI Cmin | 80% | [5 empty] | ADPI Cmin | 90% | [5 empty] | ADPI Cmin | 90% |  |  |  |  | ADPI Cmin | 95% |  |  |  |  | ADPI Cmin | 95% |  |  |  |  | ADPI Cmin | 95% |  |  |  |  | ADPI Cmin | 95% |  |  |  |  | ADPI Cmin | 95%
v' selected (turndown) | 2.8428 | L/s/m2 |  |  |  |  | v' selected (turndown) | 2.8428 | L/s/m3 |  |  |  |  | v' selected (turndown) | 2.8428 | L/s/m4 |  |  |  | v' selected (turndown) | 2.8428 | L/s/m5 |  |  |  | v' selected (turndown) | 2.8428 | L/s/m6 |  |  |  | v' selected (turndown) | 2.8428 | L/s/m7 |  |  |  | v' selected (turndown) | 2.8428 | L/s/m8 |  |  |  | v' selected (turndown) | 2.8428 | L/s/m9
Cmax Centre Zone | [6 empty] | Cmax Centre Zone | [6 empty] | Cmax Centre Zone | [5 empty] | Cmax Centre Zone | [5 empty] | Cmax Centre Zone | [5 empty] | Cmax Centre Zone | [5 empty] | Cmax Centre Zone | [5 empty] | Cmax Centre Zone
| v' | v distance | Hfactor | H distance |  |  |  | v' | v distance | Hfactor | H distance |  |  |  | v' | v distance | Hfactor | H distance |  |  | v' | v distance | Hfactor | H distance |  |  | v' | v distance | Hfactor | H distance |  |  | v' | v distance | Hfactor | H distance |  |  | v' | v distance | Hfactor | H distance |  |  | v' | v distance | Hfactor | H distance
95% | 1.1939 | 20.9402 | 5.8596 | 15.8209 |  |  | 95% | 1.7317 | 14.437 | 4.9065 | 13.2474 |  |  | 95% | 1.8954 | 13.1898 | 4.6162 | 12.4638 |  | 95% | 1.9746 | 12.6608 | 4.4759 | 12.0849 |  | 95% | 2.0243 | 12.3498 | 4.3878 | 11.847 |  | 95% | 2.0576 | 12.1498 | 4.3287 | 11.6875 |  | 95% | 2.0795 | 12.022 | 4.2899 | 11.5828 |  | 95% | 2.0968 | 11.9229 | 4.2593 | 11.5001
90% | 0.96954 | 25.7855 | 6.6122 | 17.8531 |  |  | 90% | 1.4012 | 17.8423 | 5.5367 | 14.949 |  |  | 90% | 1.5326 | 16.3122 | 5.2092 | 14.0648 |  | 90% | 1.5961 | 15.6627 | 5.0508 | 13.6372 |  | 90% | 1.6361 | 15.2806 | 4.9514 | 13.3687 |  | 90% | 1.6628 | 15.0348 | 4.8847 | 13.1887 |  | 90% | 1.6804 | 14.8778 | 4.841 | 13.0706 |  | 90% | 1.6942 | 14.7559 | 4.8064 | 12.9773
80% | 0.64028 | 39.0456 | 8.1175 | 21.9174 |  |  | 80% | 0.93119 | 26.8473 | 6.7971 | 18.3522 |  |  | 80% | 1.0198 | 24.5153 | 6.3951 | 17.2667 |  | 80% | 1.0626 | 23.5271 | 6.2007 | 16.7418 |  | 80% | 1.0895 | 22.9462 | 6.0786 | 16.4121 |  | 80% | 1.1075 | 22.5727 | 5.9967 | 16.1912 |  | 80% | 1.1194 | 22.3341 | 5.943 | 16.0462 |  | 80% | 1.1287 | 22.149 | 5.9006 | 15.9316
70% | 0.55306 | 45.203 | 9.6229 | 25.9817 |  |  | 70% | 0.8112 | 30.8187 | 8.0576 | 21.7555 |  |  | 70% | 0.8898 | 28.0963 | 7.581 | 20.4686 |  | 70% | 0.9278 | 26.9453 | 7.3505 | 19.8463 |  | 70% | 0.95167 | 26.2696 | 7.2058 | 19.4556 |  | 70% | 0.96767 | 25.8353 | 7.1088 | 19.1937 |  | 70% | 0.97817 | 25.558 | 7.0451 | 19.0218 |  | 70% | 0.98647 | 25.343 | 6.9948 | 18.8859
Compare Cmax |  | 25.7855 |  | 17.8531 |  |  | Compare Cmax |  | 17.8423 |  | 14.949 |  |  | Compare Cmax |  | 16.3122 |  | 14.0648 |  | Compare Cmax |  | 15.6627 |  | 13.6372 |  | Compare Cmax |  | 15.2806 |  | 13.3687 |  | Compare Cmax |  | 15.0348 |  | 13.1887 |  | Compare Cmax |  | 14.8778 |  | 13.0706 |  | Compare Cmax |  | 14.7559 |  | 12.9773
Recommended Cmax | 17.9 | [5 empty] | Recommended Cmax | 14.9 | [5 empty] | Recommended Cmax | 14.1 |  |  |  |  | Recommended Cmax | 13.6 |  |  |  |  | Recommended Cmax | 13.4 |  |  |  |  | Recommended Cmax | 13.2 |  |  |  |  | Recommended Cmax | 13.1 |  |  |  |  | Recommended Cmax | 13
Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies
| 95% | 15.8 | TRUE |  |  |  |  | 95% | 13.2 | TRUE |  |  |  |  | 95% | 12.5 | TRUE |  |  |  | 95% | 12.1 | TRUE |  |  |  | 95% | 11.8 | TRUE |  |  |  | 95% | 11.7 | TRUE |  |  |  | 95% | 11.6 | TRUE |  |  |  | 95% | 11.5 | TRUE
| 90% | 17.9 | TRUE |  |  |  |  | 90% | 14.9 | TRUE |  |  |  |  | 90% | 14.1 | TRUE |  |  |  | 90% | 13.6 | TRUE |  |  |  | 90% | 13.4 | TRUE |  |  |  | 90% | 13.2 | TRUE |  |  |  | 90% | 13.1 | TRUE |  |  |  | 90% | 13 | TRUE
| 80% | 21.9 | TRUE |  |  |  |  | 80% | 18.4 | TRUE |  |  |  |  | 80% | 17.3 | TRUE |  |  |  | 80% | 16.7 | TRUE |  |  |  | 80% | 16.4 | TRUE |  |  |  | 80% | 16.2 | TRUE |  |  |  | 80% | 16 | TRUE |  |  |  | 80% | 15.9 | TRUE
| 70% | 26 | TRUE |  |  |  |  | 70% | 21.8 | TRUE |  |  |  |  | 70% | 20.5 | TRUE |  |  |  | 70% | 19.8 | TRUE |  |  |  | 70% | 19.5 | TRUE |  |  |  | 70% | 19.2 | TRUE |  |  |  | 70% | 19 | TRUE |  |  |  | 70% | 18.9 | TRUE
| 0% | [6 empty] | 0% | [6 empty] | 0% | [5 empty] | 0% | [5 empty] | 0% | [5 empty] | 0% | [5 empty] | 0% | [5 empty] | 0%
ADPI Satisfied | 95% | [5 empty] | ADPI Satisfied | 95% | [5 empty] | ADPI Satisfied | 95% |  |  |  |  | ADPI Satisfied | 95% |  |  |  |  | ADPI Satisfied | 95% |  |  |  |  | ADPI Satisfied | 95% |  |  |  |  | ADPI Satisfied | 95% |  |  |  |  | ADPI Satisfied | 95%
ADPI Cmax (perimeter) | Use turndown flow rate | [5 empty] | ADPI Cmax (perimeter) | Use turndown flow rate | [5 empty] | ADPI Cmax (perimeter) | Use turndown flow rate |  |  |  |  | ADPI Cmax (perimeter) | Use turndown flow rate |  |  |  |  | ADPI Cmax (perimeter) | Use turndown flow rate |  |  |  |  | ADPI Cmax (perimeter) | Use turndown flow rate |  |  |  |  | ADPI Cmax (perimeter) | Use turndown flow rate |  |  |  |  | ADPI Cmax (perimeter) | Use turndown flow rate
Flowrates | 35 | 10.5 |  |  |  |  | Flowrates | 74 | 22.2 |  |  |  |  | Flowrates | 112 | 33.6 |  |  |  | Flowrates | 149 | 44.7 |  |  |  | Flowrates | 188 | 56.4 |  |  |  | Flowrates | 228 | 68.4 |  |  |  | Flowrates | 265 | 79.5 |  |  |  | Flowrates | 304 | 91.2
Cmax Perimeter | [6 empty] | Cmax Perimeter | [6 empty] | Cmax Perimeter | [5 empty] | Cmax Perimeter | [5 empty] | Cmax Perimeter | [5 empty] | Cmax Perimeter | [5 empty] | Cmax Perimeter | [5 empty] | Cmax Perimeter
| v' | v distance | Hfactor | H distance |  |  |  | v' | v distance | Hfactor | H distance |  |  |  | v' | v distance | Hfactor | H distance |  |  | v' | v distance | Hfactor | H distance |  |  | v' | v distance | Hfactor | H distance |  |  | v' | v distance | Hfactor | H distance |  |  | v' | v distance | Hfactor | H distance |  |  | v' | v distance | Hfactor | H distance
95% | 1.5243 | 16.4011 | 5.8596 | 15.8209 |  |  | 95% | 2.2019 | 11.3539 | 4.9065 | 13.2474 |  |  | 95% | 2.4082 | 10.3811 | 4.6162 | 12.4638 |  | 95% | 2.508 | 9.9682 | 4.4759 | 12.0849 |  | 95% | 2.5706 | 9.7252 | 4.3878 | 11.847 |  | 95% | 2.6126 | 9.5689 | 4.3287 | 11.6875 |  | 95% | 2.6402 | 9.469 | 4.2899 | 11.5828 |  | 95% | 2.662 | 9.3915 | 4.2593 | 11.5001
90% | 1.1939 | 20.9402 | 6.6122 | 17.8531 |  |  | 90% | 1.7317 | 14.437 | 5.5367 | 14.949 |  |  | 90% | 1.8954 | 13.1898 | 5.2092 | 14.0648 |  | 90% | 1.9746 | 12.6608 | 5.0508 | 13.6372 |  | 90% | 2.0243 | 12.3498 | 4.9514 | 13.3687 |  | 90% | 2.0576 | 12.1498 | 4.8847 | 13.1887 |  | 90% | 2.0795 | 12.022 | 4.841 | 13.0706 |  | 90% | 2.0968 | 11.9229 | 4.8064 | 12.9773
80% | 0.80408 | 31.0914 | 8.1175 | 21.9174 |  |  | 80% | 1.1483 | 21.772 | 6.7971 | 18.3522 |  |  | 80% | 1.2531 | 19.9511 | 6.3951 | 17.2667 |  | 80% | 1.3037 | 19.1756 | 6.2007 | 16.7418 |  | 80% | 1.3356 | 18.7187 | 6.0786 | 16.4121 |  | 80% | 1.3569 | 18.4245 | 5.9967 | 16.1912 |  | 80% | 1.3709 | 18.2363 | 5.943 | 16.0462 |  | 80% | 1.382 | 18.0903 | 5.9006 | 15.9316
70% | 0.55306 | 45.203 | 9.6229 | 25.9817 |  |  | 70% | 0.8112 | 30.8187 | 8.0576 | 21.7555 |  |  | 70% | 0.8898 | 28.0963 | 7.581 | 20.4686 |  | 70% | 0.9278 | 26.9453 | 7.3505 | 19.8463 |  | 70% | 0.95167 | 26.2696 | 7.2058 | 19.4556 |  | 70% | 0.96767 | 25.8353 | 7.1088 | 19.1937 |  | 70% | 0.97817 | 25.558 | 7.0451 | 19.0218 |  | 70% | 0.98647 | 25.343 | 6.9948 | 18.8859
Compare Cmax |  | 20.9402 |  | 17.8531 |  |  | Compare Cmax |  | 14.437 |  | 14.949 |  |  | Compare Cmax |  | 13.1898 |  | 14.0648 |  | Compare Cmax |  | 12.6608 |  | 13.6372 |  | Compare Cmax |  | 12.3498 |  | 13.3687 |  | Compare Cmax |  | 12.1498 |  | 13.1887 |  | Compare Cmax |  | 12.022 |  | 13.0706 |  | Compare Cmax |  | 11.9229 |  | 12.9773
Recommended Cmax | 17.9 | [5 empty] | Recommended Cmax | 14.4 | [5 empty] | Recommended Cmax | 13.2 |  |  |  |  | Recommended Cmax | 12.7 |  |  |  |  | Recommended Cmax | 12.3 |  |  |  |  | Recommended Cmax | 12.1 |  |  |  |  | Recommended Cmax | 12 |  |  |  |  | Recommended Cmax | 11.9
Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies |  |  | Resultant ADPI from selected Cmax | ADPI | Selected Dist | Selected C Satisfies
| 95% | 15.8 | TRUE |  |  |  |  | 95% | 11.4 | TRUE |  |  |  |  | 95% | 10.4 | TRUE |  |  |  | 95% | 10 | TRUE |  |  |  | 95% | 9.7 | TRUE |  |  |  | 95% | 9.6 | TRUE |  |  |  | 95% | 9.5 | TRUE |  |  |  | 95% | 9.4 | TRUE
| 90% | 17.9 | TRUE |  |  |  |  | 90% | 14.4 | TRUE |  |  |  |  | 90% | 13.2 | TRUE |  |  |  | 90% | 12.7 | TRUE |  |  |  | 90% | 12.3 | TRUE |  |  |  | 90% | 12.1 | TRUE |  |  |  | 90% | 12 | TRUE |  |  |  | 90% | 11.9 | TRUE
| 80% | 21.9 | TRUE |  |  |  |  | 80% | 18.4 | TRUE |  |  |  |  | 80% | 17.3 | TRUE |  |  |  | 80% | 16.7 | TRUE |  |  |  | 80% | 16.4 | TRUE |  |  |  | 80% | 16.2 | TRUE |  |  |  | 80% | 16 | TRUE |  |  |  | 80% | 15.9 | TRUE
| 70% | 26 | TRUE |  |  |  |  | 70% | 21.8 | TRUE |  |  |  |  | 70% | 20.5 | TRUE |  |  |  | 70% | 19.8 | TRUE |  |  |  | 70% | 19.5 | TRUE |  |  |  | 70% | 19.2 | TRUE |  |  |  | 70% | 19 | TRUE |  |  |  | 70% | 18.9 | TRUE
| 0% | [6 empty] | 0% | [6 empty] | 0% | [5 empty] | 0% | [5 empty] | 0% | [5 empty] | 0% | [5 empty] | 0% | [5 empty] | 0%
ADPI Satisfied | 95% | [5 empty] | ADPI Satisfied | 95% | [5 empty] | ADPI Satisfied | 95% |  |  |  |  | ADPI Satisfied | 95% |  |  |  |  | ADPI Satisfied | 95% |  |  |  |  | ADPI Satisfied | 95% |  |  |  |  | ADPI Satisfied | 95% |  |  |  |  | ADPI Satisfied | 95%
COMBINED SELECTED ADPI (Centre) | 80% | [5 empty] | COMBINED SELECTED ADPI (Centre) | 90% | [5 empty] | COMBINED SELECTED ADPI (Centre) | 90% |  |  |  |  | COMBINED SELECTED ADPI (Centre) | 95% |  |  |  |  | COMBINED SELECTED ADPI (Centre) | 95% |  |  |  |  | COMBINED SELECTED ADPI (Centre) | 95% |  |  |  |  | COMBINED SELECTED ADPI (Centre) | 95% |  |  |  |  | COMBINED SELECTED ADPI (Centre) | 95%
COMBINED SELECTED ADPI (Perim) | 80% | [5 empty] | COMBINED SELECTED ADPI (Perim) | 90% | [5 empty] | COMBINED SELECTED ADPI (Perim) | 90% |  |  |  |  | COMBINED SELECTED ADPI (Perim) | 95% |  |  |  |  | COMBINED SELECTED ADPI (Perim) | 95% |  |  |  |  | COMBINED SELECTED ADPI (Perim) | 95% |  |  |  |  | COMBINED SELECTED ADPI (Perim) | 95% |  |  |  |  | COMBINED SELECTED ADPI (Perim) | 95%
Heating | [6 empty] | Heating | [6 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating
heatingX | 12.556 |  | -0.000743 | 0.2132 | -1.334 |  | heatingX | 10.473 |  | -0.0003741 | 0.1538 | -1.166 |  | heatingX | 8.654 |  | -0.0002393 | 0.1218 | -1.133 | heatingX | 7.655 |  | -0.0001794 | 0.1058 | -1.131 | heatingX | 6.757 |  | -0.0001424 | 0.0949 | -1.309 | heatingX | 6.03 |  | -0.0001049 | 0.08228 | -1.149 | heatingX | 5.462 |  | -0.0001196 | 0.08413 | -1.755 | heatingX | 4.954 |  | -0.0001152 | 0.08117 | -2.011
heatingSlope | 0.65159 | [5 empty] | heatingSlope | 0.65159 | [5 empty] | heatingSlope | 0.65159 |  |  |  |  | heatingSlope | 0.65159 |  |  |  |  | heatingSlope | 0.65159 |  |  |  |  | heatingSlope | 0.65159 |  |  |  |  | heatingSlope | 0.65159 |  |  |  |  | heatingSlope | 0.65159
heatingY | 8.1814 | [5 empty] | heatingY | 6.8241 | [5 empty] | heatingY | 5.6389 |  |  |  |  | heatingY | 4.9879 |  |  |  |  | heatingY | 4.4028 |  |  |  |  | heatingY | 3.9291 |  |  |  |  | heatingY | 3.559 |  |  |  |  | heatingY | 3.228
heating_dT(10K) | 18.1809 |  |  | 2.2222 |  |  | heating_dT(10K) | 15.1632 |  |  | 2.222 |  |  | heating_dT(10K) | 12.5296 |  |  | 2.222 |  | heating_dT(10K) | 11.0832 |  |  | 2.222 |  | heating_dT(10K) | 9.783 |  |  | 2.222 |  | heating_dT(10K) | 8.7305 |  |  | 2.222 |  | heating_dT(10K) | 7.9081 |  |  | 2.222 |  | heating_dT(10K) | 7.1726 |  |  | 2.222
(old) heating @ dT | 16.2648 | [5 empty] | (old) heating @ dT | 13.5651 | [5 empty] | (old) heating @ dT | 11.2091 |  |  |  |  | (old) heating @ dT | 9.9151 |  |  |  |  | (old) heating @ dT | 8.752 |  |  |  |  | (old) heating @ dT | 7.8104 |  |  |  |  | (old) heating @ dT | 7.0746 |  |  |  |  | (old) heating @ dT | 6.4167
heating dT (perimeter) | 32.5295 | [5 empty] | heating dT (perimeter) | 27.1303 | [5 empty] | heating dT (perimeter) | 22.4182 |  |  |  |  | heating dT (perimeter) | 19.8303 |  |  |  |  | heating dT (perimeter) | 17.504 |  |  |  |  | heating dT (perimeter) | 15.6207 |  |  |  |  | heating dT (perimeter) | 14.1493 |  |  |  |  | heating dT (perimeter) | 12.8333
heating dT (centre) | 48.7943 | [5 empty] | heating dT (centre) | 40.6954 | [5 empty] | heating dT (centre) | 33.6273 |  |  |  |  | heating dT (centre) | 29.7454 |  |  |  |  | heating dT (centre) | 26.256 |  |  |  |  | heating dT (centre) | 23.4311 |  |  |  |  | heating dT (centre) | 21.2239 |  |  |  |  | heating dT (centre) | 19.25
heating dT 'E' | 65.0591 | [5 empty] | heating dT 'E' | 54.2606 | [5 empty] | heating dT 'E' | 44.8363 |  |  |  |  | heating dT 'E' | 39.6605 |  |  |  |  | heating dT 'E' | 35.008 |  |  |  |  | heating dT 'E' | 31.2414 |  |  |  |  | heating dT 'E' | 28.2986 |  |  |  |  | heating dT 'E' | 25.6667
Vertical Penetration Eqn | [6 empty] | Vertical Penetration Eqn | [6 empty] | Vertical Penetration Eqn | [5 empty] | Vertical Penetration Eqn | [5 empty] | Vertical Penetration Eqn | [5 empty] | Vertical Penetration Eqn | [5 empty] | Vertical Penetration Eqn | [5 empty] | Vertical Penetration Eqn
k-factor | 1.2 | [5 empty] | k-factor | 1.03 | [5 empty] | k-factor | 0.97 |  |  |  |  | k-factor | 0.92 |  |  |  |  | k-factor | 0.88 |  |  |  |  | k-factor | 0.85 |  |  |  |  | k-factor | 0.83 |  |  |  |  | k-factor | 0.81
H-n (exit width) | 0.013 | [5 empty] | H-n (exit width) | 0.026 | [5 empty] | H-n (exit width) | 0.039 |  |  |  |  | H-n (exit width) | 0.052 |  |  |  |  | H-n (exit width) | 0.065 |  |  |  |  | H-n (exit width) | 0.078 |  |  |  |  | H-n (exit width) | 0.091 |  |  |  |  | H-n (exit width) | 0.104
dT (Vertical) | 168.1756 | K |  |  |  |  | dT (Vertical) | 47.2827 | K |  |  |  |  | dT (Vertical) | 23.5216 | K |  |  |  | dT (Vertical) | 14.1118 | K |  |  |  | dT (Vertical) | 9.4463 | K |  |  |  | dT (Vertical) | 6.8217 | K |  |  |  | dT (Vertical) | 5.2235 | K |  |  |  | dT (Vertical) | 4.1218 | K
dT (Vertical) Low level corrected | 168.1756 | K |  |  |  |  | dT (Vertical) Low level corrected | 47.2827 | K |  |  |  |  | dT (Vertical) Low level corrected | 23.5216 | K |  |  |  | dT (Vertical) Low level corrected | 14.1118 | K |  |  |  | dT (Vertical) Low level corrected | 9.4463 | K |  |  |  | dT (Vertical) Low level corrected | 6.8217 | K |  |  |  | dT (Vertical) Low level corrected | 5.2235 | K |  |  |  | dT (Vertical) Low level corrected | 4.1218 | K
Horizontal > Vertical | 168.1756 | K |  |  |  |  | Horizontal > Vertical | 47.2827 | [5 empty] | Horizontal > Vertical | 33.6273 |  |  |  |  | Horizontal > Vertical | 29.7454 |  |  |  |  | Horizontal > Vertical | 26.256 |  |  |  |  | Horizontal > Vertical | 23.4311 |  |  |  |  | Horizontal > Vertical | 21.2239 |  |  |  |  | Horizontal > Vertical | 19.25
1Slot | [6 empty] | 2Slot | [6 empty] | 3Slot | [5 empty] | 4Slot | [5 empty] | 5Slot | [5 empty] | 6Slot | [5 empty] | 7Slot | [5 empty] | 8Slot
Heating Constant Quadratic Curve
-0.00451 | 0.09517 | 0.4993
Global Distance | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Cmin | 17.8531 | 14.437 | 13.1898 | 12.6608 | 12.3498 | 12.1498 | 12.022 | 11.9229
Cmax | 16.8073 | 6.4501 | 5.431 | 5.0455 | 4.8302 | 4.6959 | 4.6118 | 4.5474
Accept | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE
Accept cmax |  |  | 13.1898 | 12.6608 | 12.3498 | 12.1498 |  |  | 12.5876
accept cmin |  |  | 5.431 | 5.0455 | 4.8302 | 4.6959 |  |  | 5.0007
if all rejected | 17.8531 | 14.437 | 13.1898 | 12.6608 | 12.3498 | 12.1498 | 12.022 | 11.9229 | 13.3232
if all rejected | 16.8073 | 6.4501 | 5.431 | 5.0455 | 4.8302 | 4.6959 | 4.6118 | 4.5474 | 6.5524
Average | 8.7941
Final Distance Selections
Selected Dist | 8.7941
diffuser dist from spec. afr | 10
diffuser dist from spec. afr (td) | 5 | ?? Not sure if needed
diffuser dist selected | 8.7941 | m
Area (incl active length) | 17.5883 | m2
v" (incl active length) | 5.6856 | L/s/m2
v" (incl active length) (for display/units) | 5.6856 | L/s/m²
turndown v" | 2.8428 | L/s/m2
V'' adjusted for heating | 5.6856 | L/s/m2
Air Pattern Settings | 2 WAY | 1 WAY
1 | A | AB | A
2 | B | AC | B
3 | C | BC | C
A
Pre-Results
Slots | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Max Airflow (L/s/m) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Max Recommended Airflow (L/s) | 33.5767 | 70.6866 | 108.7646 | 143.645 | 185.9433 | 228.9278 | 262.348 | 308.019
Min Airflow (L/s/m) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Min Permissible Airflow | 7.5777 | 16.0215 | 24.2487 | 32.2594 | 40.7032 | 49.3634 | 57.3742 | 65.8179
Min % Turndown to | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50%
Min Permissible % Turndown to | 7.578% | 16.02% | 24.25% | 32.26% | 40.7% | 49.36% | 0.57374 | 0.65818
Max Static Pressure (Pa) | 266.1005 | 60.0409 | 25.3598 | 14.5392 | 8.6768 | 5.7243 | 4.3588 | 3.162
Max Total Pressure (Pa) | 272.3064 | 66.2469 | 31.5658 | 20.7451 | 14.8827 | 11.9302 | 10.5647 | 9.368
Max Permissible Pressure (Pa) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Sound Power Level (dBA) | 48.3753 | 41.2423 | 34.3719 | 27.9098 | 22.6896 | 16.3539 | 13.123 | 9.1092
Sound Pressure Level (NC) | 33.3753 | 26.2423 | 19.3719 | 12.9098 | 7.6896 | 1.3539 | -1.877 | -5.8908
Max Permissible ΔT (centre) (K) | 48.7943 | 40.6954 | 33.6273 | 29.7454 | 26.256 | 23.4311 | 21.2239 | 19.25
Max Permissible ΔT (heating) (K) | 32.5295 | 27.1303 | 22.4182 | 19.8303 | 17.504 | 15.6207 | 14.1493 | 12.8333
Max Permissible ΔT ('E') (K) | 168.1756 | 47.2827 | 33.6273 | 29.7454 | 26.256 | 23.4311 | 21.2239 | 19.25
Max Coverage Dist Centre Zone | 17.8531 | 14.949 | 14.0648 | 13.6372 | 13.3687 | 13.1887 | 13.0706 | 12.9773
Max C/L Distance (m) Perimeter | 17.8531 | 14.437 | 13.1898 | 12.6608 | 12.3498 | 12.1498 | 12.022 | 11.9229
Min C/L Distance (m) | 16.8073 | 6.4501 | 5.431 | 5.0455 | 4.8302 | 4.6959 | 4.6118 | 4.5474
Min Diffuser Height (m) | 2.4581 | 2.5128 | 2.5674 | 2.622 | 2.6766 | 2.7313 | 2.7859 | 2.8405
Air Pattern Setting | A | A | A | A | A | A | A | A
Mean Room Air V | 19.82% | 0.16674 | 0.15552 | 0.14971 | 0.14591 | 0.1433 | 0.14155 | 0.14014
Draught Rating | 20.46% | 0.16287 | 0.14845 | 0.14107 | 0.13627 | 0.13297 | 0.13077 | 0.12901
PPD | 10.21% | 0.083982 | 0.078132 | 0.075217 | 0.073351 | 0.072083 | 0.071244 | 0.070575
PPD Class | C | B | B | B | B | B | B | B
PMV | 0.5 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3
Nominal Spigot Size | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200
ADPI actual (centre) | 80% | 90% | 90% | 95% | 95% | 95% | 95% | 95%
ADPI actual (perim) | 80% | 90% | 90% | 95% | 95% | 95% | 95% | 95%
| 12.556 | 10.473 | 8.654 | 7.655 | 6.757 | 6.03 | 5.462 | 4.954
Results
Slots | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Selected Airflow [L/s/m] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Airflow @ Max Static Pressure[L/s/m] | 34 | 71 | 109 | 144 | 186 | 229 | 262 | 308
Min Selected Airflow [L/s/m] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Min Permissible Airflow @ -12 K | 7.6 | 16 | 24.2 | 32.3 | 40.7 | 49.4 | 57.4 | 65.8
Min % Turndown to | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Min Permissible % Turndown to | 8% | 16% | 24% | 32% | 41% | 49% | 57% | 66%
Max Static Pressure (Pa) | 266.1 | 60 | 25.4 | 14.5 | 8.7 | 5.7 | < 4.5 | < 4.5
Max Total Pressure (Pa) | 272.3 | 66.2 | 31.6 | 20.7 | 14.9 | 11.9 | 10.6 | 9.4
Max Permissible Pressure (Pa) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Sound Power Level (dBA) | 48.4 | 41.2 | 34.4 | 27.9 | 22.7 | 16.4 | < 15 | < 15
Sound Pressure Level (NC) | 33.4 | 26.2 | 19.4 | 12.9 | < 10 | < 10 | < 10 | < 10
Centre Zone: Setting 'A' | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | Centre Zones for Air Direction 'A' [K]
Perimeter Zone: Setting 'A' | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | Perimeter Zones for Air Direction 'A' [K]
Max Permissible ΔT (heating) E (K) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | Max Permissible ΔT (heating) E (K)
Max Coverage Dist Centre Zone | 17.9 | 14.9 | 14.1 | 13.6 | 13.4 | 13.2 | 13.1 | 13
Max C/L Distance (m) Perimeter | 17.9 | 14.4 | 13.2 | 12.7 | 12.3 | 12.1 | 12 | 11.9
Min C/L Distance (m) | 16.8 | 6.5 | 5.4 | 5 | 4.8 | 4.7 | 4.6 | 4.5
Min Diffuser Height (m) | 2.5 | 2.5 | 2.6 | 2.6 | 2.7 | 2.7 | 2.8 | 2.8
Air Pattern Setting | bar: 8% to 66%
Mean Room Air V | 0.2 | 0.17 | 0.16 | 0.15 | 0.15 | 0.14 | 0.14 | 0.14
Draught Rating | 20.5% | 16.3% | 14.8% | 14.1% | 13.6% | 13.3% | 13.1% | 12.9%
PPD | 10.2% | 8.4% | 7.8% | 7.5% | 7.3% | 7.2% | 7.1% | 7.1%
PMV | 0.5 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3
PPD Class | bar: 8% to 66%
Nominal Spigot Size | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200
ADPI actual (centre) | 80% | 90% | 90% | 95% | 95% | 95% | 95% | 95%
ADPI actual (perim) | 80% | 90% | 90% | 95% | 95% | 95% | 95% | 95%
Shading
max flow | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE |  | True = Shade
min flow | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
cmin>cmax centre | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE |  | true = shade
cmin>cmax perim | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
selected dist < cmin | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
Shade | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
Draft Rating
Max Spec Flowrate | 8%: 30

## Notes
SMARTEMP PRODUCT SELECTION CALCULATOR
Linear Multistream Ceiling Diffuser [LMC-AD] Notes
Notes
Pressure is inclusive of side-entry connection box pressure loss.
Centreline distance is the spacing between two 2-way blow diffuser rows. Halve this value for throw to walls or maximum throw of a 1-way diffuser. Refer to Diffuser Location notes below.
Select desired comfort level (ADPI setting) to determine minimum and maximum spacing or throw (centreline distances) and minimum discharge height.
Sound pressure level [NC] is valid in a standard commercial office with a 2.7 m to 3 m ceiling.
Inputs
Active Length Ratio = LA / L |  | where: | LA = ∑ LA,i | and | e.g. | Active Length Ratio | = (1.2+1.2)/4.8
|  |  | LA ≥ 0.1 ∙ L |  |  |  | = 0.5
Refer to Fig. 1, Fig. 2 for description of lengths 'L' and 'LA'
Layout/Coverage Distances
|  |  |  | For 2-Way Discharge |  |  |  | For 1-Way Discharge
Air Direction Settings
A | 0⁰ to -15⁰ discharge to the horizontal
B | 0⁰ to -30⁰ discharge to the horizontal
C | ≈ -45⁰ discharge to the horizontal
D | ≈ -60⁰ discharge to the horizontal
E | vertical discharge
Sound
Sound Pressure Level (NC/m) based on 10 dB room absorption
Air Direction D
Air Direction A
Air Direction B
Air Direction C
0 to -15°
0 to -30°
≈ -45°
≈ -60°

## Diffuser Layout (hidden)
SMARTEMP PRODUCT SELECTION CALCULATOR
Linear Multistream Ceiling Diffuser [LMC-AD] Notes
Notes
Total pressure is inclusive of side-entry connection box pressure loss.
Centreline distance is the spacing between two 2-way blow diffuser rows. Halve this value for throw to walls or maximum throw of a 1-way diffuser. Refer to Diffuser Location notes below.
Select desired comfort level (ADPI setting) to determine minimum and maximum spacing or throw (centreline distances) and minimum discharge height.
Sound pressure level [NC] is valid in a standard commercial office with a 2.7 m to 3 m ceiling.
Inputs
Active Length Ratio = LA / L |  |  | where: | LA = ∑ LA,i | and | e.g. |  | Active Length Ratio | = (1.2+1.2)/4.8
|  |  |  | LA ≥ 0.1 ∙ L |  |  |  |  | = 0.5
Refer to Fig. 1, Fig. 2 for description of lengths 'L' and 'LA'
Diffuser Distance
| For 2-Way Blow |  | 100 | L/s/m |  |  | For 1-Way Blow (not selected) |  |  | 100 | L/s/m
| C | #REF!
| C/2 | #REF!
C/4
C/8
ALL DIMENSIONS IN m
Air Direction Settings
A | 0⁰ to -15⁰ discharge to the horizontal
B | 0⁰ to -30⁰ discharge to the horizontal
C | ≈ -45⁰ discharge to the horizontal
D | ≈ -60⁰ discharge to the horizontal
Sound
Sound Pressure Level (NC/m) based on 10 dB room absorption
Air Direction D
#REF!
#REF!
Figure 1
Figure 2
Air Direction A
Air Direction B
Air Direction C
1.2 m
1.2 m
4.8 m
0 to -15°
0 to -30°
≈ -45°
≈ -60°

## Dimensions
SMARTEMP PRODUCT SELECTION CALCULATOR
Linear Multistream Ceiling Diffuser [LMC-AD] Dimensions
Dimensions
|  |  |  | 1 Slot | 2 Slots | 3 Slots | 4 Slots | 5 Slots | 6 Slots | 7 Slots | 8 Slots
|  | Width Flangeless Face (Wn) |  | 31 | 59 | 87 | 115 | 143 | 171 | 199 | 227 | mm
|  | Width Flanged Face (Wf) |  | 48 | 76 | 104 | 132 | 160 | 188 | 216 | 244 | mm
|  | Width of Diffuser Throat (Wt) |  | 27 | 55 | 83 | 111 | 139 | 167 | 195 | 223 | mm
|  | Recommended Plenum Height A * |  | D + 76 | [7 empty] | mm
|  | Recommended Plenum Width B * |  | 81 | 109 | 137 | 165 | 193 | 221 | 249 | 277 | mm
|  | Recommended Spigot Dimension D * per 1 m length |  | 124 | 179 | 224 | 249 | 299 | 299 | 314 | 349 | mm
|  | Recommended Spigot Dimension D * per 1.2 m length |  | 149 | 199 | 224 | 299 | 299 | 314 | 349 | 399 | mm
|  | Recommended Spigot Dimension D * per 1.5 m length |  | 149 | 224 | 249 | 299 | 314 | 349 | 399 | - | mm
|  |  | * | Plenum box dimensions are for internal dimensions (excludes insulation and acoustic lining)
|  |  | * | Check exact dimensions with local supplier

## data (hidden)
ADPI
95% | 0.2
90% | 0.25
80% | 0.29
70% | 0.33 |  |  | 1 | N1200 | Neck
|  |  |  | 2 | F1195 | Face
Length | F1195 | 2 | Face | 3 | <length> | face length
nslots | 2 | 2
Supply Return
Radio Input | 1
Type | Supply | AD |  | Linear Multistream Adjustable Diffuser
| Return | RA | - Diffuser perfomance data not applicable for return grille | Linear Multistream Return Air Grille | Note: Diffuser perfomance data not applicable for return grille
Selection | Supply | AD |  | Linear Multistream Adjustable Diffuser
airpatternnum | 2
| 1 | 2 | 3 | 4 | 5 | 6 | 7
1way text | recommended | AB | AC | BC | BD | EE (vertical) | custom
2way text | recommended | A* (0 to -15°) | B (0 to -30°) | C (≈ -45°) | D (≈ -60°) | E (vertical) | custom
2way text | recommended | A* (0 to -15°) | B (0 to -30°) | C (≈ -45°) | D (≈ -60°) | E (vertical) | custom
1way code |  | AB | AC | BC | BD | EE | <direction>
2way code |  | A | B | C | D | E | <direction>
Result | A | A | B | C | D | E | <direction>
airpatterletter | A | 1
Colour | RAL9003 | 1 | RAL9005 (jet black)
Barrel | B | 1
Side Profile |  | Code | Description
| 1 | SF | with side flanges
| 2 | SN | flangeless side profile
Selection | 1 | SF | with side flanges
Diffuser Ends
|  | Code | Description
| 1 | E2 | with two end flanges
| 2 | E1 | with one end flange + one pair of joining strips
| 3 | EJ | include one pair of joining strips
| 4 | E0 | without end flanges
Selection | 1 | E2 | with two end flanges
Fixing |  | Code | Description
| 1 | F0 | fixing by others; without accessories
| 2 | EX | expansion bracket fixing
| 3 | MFP | mounting frame for plasterboard
Selection | 3 | MFP | mounting frame for plasterboard
connection box
| 1 | K0 | no connection box
| 2 | K | uninsulated connection box
| 3 | KI | internally insulated connection box
Selection | 1 | K0 | no connection box
0
| 1 | t | clipped to diffuser throat
| 2 | n | screwed to diffuser throat
Selection | 1
0
Selection |  | K0 | no connection box
Naming
| nominal length | nslots | airpattern num | airpattern letter | profile type | diffuserends | fixing | profile colour | barrelcolour | Box
SMARTEMP LMC-AD- | F1195- | 2- | 2 | A- | SF- | E2- | MFP- | RAL9003- | B- | K0
AD: | SMARTEMP LMC-AD-F1195-2-2A-SF-E2-MFP-RAL9003-B-K0
RA: | SMARTEMP LMC-AD-F1195-2-SF-E2-MFP-RAL9003-B-K0
CODE | SMARTEMP LMC-AD-F1195-2-2A-SF-E2-MFP-RAL9003-B-K0
Type | SMARTEMP LMC-AD
Bespoke dimensions
Summary
Length | Face 1195 mm
Slots | 2
Size | Face 1195 mm × 2 slots
Air pattern | 2-way blow
Location | Closed Ceiling
Description | 1195 mm face length with 2 slots | 1195 mm face length | 2 slots
2-way blow with discharge direction 'A'
with side flanges
with two end flanges
mounting frame for plasterboard
| profile powder coated to RAL9003 with black barrels | RAL9003 | black
no connection box
Format
0 | Slots | 2
1 | Selected Airflow [L/s/m] | 100
2 | Airflow @ Max Static Pressure[L/s/m] | 71
3 | Min Selected Airflow [L/s/m] | 50
4 | Min Permissible Airflow [L/s/m] | 16
5 | Min % Turndown to | 0.5 | 50
6 | Min Permissible % Turndown to | 0.16
7 | Max Static Pressure (Pa) | 60
8 | Max Total Pressure (Pa) | 66.2
9 | Max Permissible Pressure (Pa) | 30
10 | Sound Power Level (dBA) | 41.2
11 | Sound Pressure Level (NC) | 26.2
12 | Centre Zones for Air Direction 'A' [K] | 10
13 | Perimeter Zones for Air Direction 'A' [K] | 10
14 | Max Permissible ΔT (heating) E (K) | 15
15 | Max Centre C/L Distance (m) | 14.9
16 | Max Perim C/L Distance (m) | 14.4
17 | Min C/L Distance (m) | 6.5
18 | Min Diffuser Height (m) | 2.5
19 | Air Pattern Setting | A
20 | Mean Room Air V | 0.17
21 | Draught Rating | 0.163
22 | PPD | 0.084
23 | PMV | 0.4
24 | PPD Class | B
25 | Nominal Spigot Size | DN200
26 | ADPI actual (centre) | 90% | ≥ 90% (for centre zones)
27 | ADPI actual (perim) | 90% | ≥ 90% (for perimeter zones)
dt | -12
room temp | 23
dist type selection | 1
height | 2.7
Units | L/s/m | L/s/m²
Summary
Text
Airflow | 100 L/s/m @ 66.2 Pa total (60 Pa static)
Min airflow | 50 L/s/m (50% turndown to) @ ΔT = -12 K
Heating non vertical | + 10 K for centre zones; + 10 K for perimeter zones (pattern 'A')
Heating vertical | + 15 K for vertical discharge (pattern 'E')
Max Heating | + 10 K for centre zones; + 10 K for perimeter zones (pattern 'A')
Suggested Air Direction Setting | 2-way blow, setting 'A'
Acoustic
SWL | 41.2 dB(A)/m
SPL | 26.2 NC/m
Recommended Plenum Box Spigot Diameter per (1200 mm length) | DN200 mm
Comfort
ADPI | ≥ 90% (for centre zones) // ≥ 90% (for perimeter zones)
Mean Room Air Velocity | 0.17 m/s
Mean Draught Rating | 16.3% @ room temperature of 23°C
Mean PPD | 8.4%
Satisfies PPD (ISO7730) | Category B
Mean PMV * | -0.4 < PMV < +0.4
Diagram
Selected ADPI | Recommended distances for ≥ 90% ADPI (Selected)
Cmin | 6.5
Cmax Cenre | 14.9 m
Cmax Perim | 14.4 m
Text | C Max (centre/perimeter) = 14.9 m/14.4 m
C Min = 6.5 m
Average
C Select | 8.8 | m
| 5.7 | L/s/m²
Average C = 8.8 m
box1 | C Max (centre/perimeter) = 14.9 m/14.4 m | 1 | Specific Airflow Rate @ Average C of 8.8 m: 5.7 L/s/m²
box2 | C Min = 6.5 m | 2 | Specific Airflow Rate @ Selected C of 8.8 m: 5.7 L/s/m²
box3 | Average C = 8.8 m | 3 | Specific Airflow Rate = 5.7 L/s/m²
room box | Specific Airflow Rate @ Average C of 8.8 m: 5.7 L/s/m²
Height | Selected Diffuser Height = 2.7 m
Min Recommended Diffuser Height = 2.5 m

## Selection Summary
LMC-AD Performance Calculator Summary
v 8.0 [08/2023]
Project | <Project Name>
Diffuser Location | <Name>
Consultant | <Name>
Product | SMARTEMP LMC-AD
Linear Multistream Adjustable Diffuser
Size | Face 1195 mm × 2 slots
Discharge Direction | 2-way blow
Diffuser Location | Closed Ceiling
Summary
Selected Airflow | 100 L/s/m @ 66.2 Pa total (60 Pa static)
Min Selected Airflow | 50 L/s/m (50% turndown to) @ ΔT = -12 K
Max Recommended Heating ΔT | + 10 K for centre zones; + 10 K for perimeter zones (pattern 'A')
Selected Air Discharge Setting | 2-way blow, setting 'A'
Acoustic Performance
Sound Power Level | 41.2 dB(A)/m
Sound Pressure Level ^ | 26.2 NC/m | ^ based on 10dB room absorption
Recommended Plenum Box Spigot Diameter (per 1200 mm length) | DN200 mm
Comfort Performance
ADPI | ≥ 90% (for centre zones) // ≥ 90% (for perimeter zones)
Mean Room Air Velocity | 0.17 m/s
Mean Draught Rating | 16.3% @ room temperature of 23°C
Mean PPD | 8.4%
Satisfies PPD (ISO7730) | Category B
Mean PMV * | -0.4 < PMV < +0.4
* ISO7730; ASHRAE Std 55
Description | 1195 mm face length with 2 slots
2-way blow with discharge direction 'A'
with side flanges
with two end flanges
mounting frame for plasterboard
profile powder coated to RAL9003 with black barrels
no connection box
Order Code | SMARTEMP LMC-AD-F1195-2-2A-SF-E2-MFP-RAL9003-B-K0
C Max (centre/perimeter) = 14.9 m/14.4 m
Average C = 8.8 m
C Min = 6.5 m
Min Recommended Diffuser Height = 2.5 m
Specific Airflow Rate @ Average C of 8.8 m: 5.7 L/s/m²
Selected Diffuser Height = 2.7 m
Recommended distances for ≥ 90% ADPI (Selected)