## HSC-AD
SMARTEMP PRODUCT SELECTION CALCULATOR
Adjustable Helical Swirl Diffuser [HSC-AD]
Project: | <Name>
| Inputs | [6 empty] | Detailed Selection | [14 empty] | v 7.15 [01/25]
| Diffuser Airflow Rate | 800 |  | [L/s] | [m3/h] |  |  |  | ADPI ≥ | 90% |  | default ≥ 90% (ADPI valid for cooling mode only)
|  | = 2880 | m³/h
| Turndown to | 100 | % | use 100% for CAV |  |  |  | Draught Rating & Heating
| Maximum Static Pressure | 60 | Pa | default 60 Pa | [5 empty] | Average Recommended Diffuser Coverage |  | See Rows 50 to 52
[8 empty] | OR |  | nominal distance = 11.5 | m
| Diffuser Height | 6 | m | 2 m ≤ height ≤ 20 m (heating and cooling) |  |  |  |  | Manual Diffuser Coverage | 20 | m | see layout diagram below
|  |  |  | 2 m ≤ height ≤ 26 m (cooling only) |  |  |  | OR |  | = specific airflow rate: 6.1 | L/s/m²
[9 empty] | Specific Airflow Rate | 10 | L/s/m² | ≤ 30 L/s/m²
| ΔT supply (cooling) | -12 | K | 0 K to -15 K (default -12 K) | [5 empty] | average diffuser coverage distance: 11.5 | m
[9 empty] | Diffuser Location | Closed Ceiling |  | Freely Suspended (≥ 600mm below ceiling)
[9 empty] | ΔT supply (heating) | 4 | K | check for manual supply temperature input
[9 empty] | Room Temperature (cooling) | 23 | °C | 20 °C to 26 °C
[9 empty] | Room Temperature (heating) | 22 | °C | check for manual input
[10 empty] | auto room temp. (heating) = 21 | °C
[9 empty] | Room Temp. @ heating startup | 16 | °C | night setback temperature (default 16°C)
[9 empty] | % Low Level Return (heating) | 0% |  | 0% to 100% (default 0%)
Related Products
Smartemp JSC-AD: | for use in ultra high ceilings; increased heating penetration also with electric and thermal actuator | [6 empty] | Thermal Comfort Guide
Smartemp LJC-AD: | for a linear-slot solution also with electric and thermal actuator | [6 empty] | ADPI ≥ 95%; ṽ ≤ 0.20 m/s: | Premium comfort, sedentary activity, such as in auditoria.
[8 empty] | ADPI ≥ 90%; ṽ ≤ 0.25 m/s: | High comfort near-sedentary activity, such as in board rooms, high end offices and libraries.
[8 empty] | ADPI ≥ 80%; ṽ ≤ 0.29 m/s: | Good comfort near sedentary activity, such as open-plan offices and meeting rooms.
[8 empty] | ADPI ≥ 70%; ṽ ≤ 0.33 m/s: | Standard comfort medium activity, such as in transient spaces, retail and lobbies.
[8 empty] | ex-factory only |  |  | ex-factory only |  |  | not available in all regions |  | FUSION DN1340 | Key: | Suitable | Not Suitable | Warning | Note: | R0 - no reducer; R1 - with reducer
SMARTEMP HSC-AD- |  |  |  | DN250-R1 | DN250-R0 | DN355-R1 | DN355-R0 | DN400-R0 | DN500-R1 | DN500-R0 | DN630-R0 | DN710-R1 | DN710-R0 | DN1000-R1 | DN1000-R0
Airflow | Selected Airflow |  | [L/s] | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800
| Airflow @ Selected Pressure |  | [L/s] | 191.9945 | 218.6273 | 384.8618 | 508.5015 | 608.5517 | 702.3724 | 851.5494 | 1351.3906 | 1416.2637 | 1717.0641 | 2809.4896 | 3406.1975 | 6116.1682
| Selected Minimum Airflow |  | [L/s] | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800
| Min Permissible Airflow |  | [L/s] | 69.764 | 77.896 | 134.07 | 168.92 | 204.59 | 247.23 | 291.92 | 463.3 | 498.5146 | 588.6275 | 988.92 | 1167.68 | 1803.6414
Pressure | Static Pressure @ Selected Airflow |  | [Pa] | 1041.7266 | 803.3824 | 259.2518 | 148.5069 | 103.6899 | 77.8388 | 52.9556 | 21.0266 | 19.1445 | 13.0244 | 4.8649 | < 5 | < 5
| Total Pressure @ Selected Airflow |  | [Pa] | 1204.4112 | 966.0669 | 299.264 | 188.5192 | 128.5135 | 88.0066 | 63.1233 | 25.0607 | 21.6452 | 15.5252 | < 10 | < 10 | < 10
| Max Permissible Static Pressure |  | [Pa] | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Acoustic | Sound Power Level |  | [dB(A)] | 94.469 | 89.6589 | 79.3317 | 69.3862 | 64.0676 | 59.7736 | 54.2033 | 42.9678 | 41.1913 | 37.3153 | 24.6117 | 20.7295 | < 20
Heating | Max Recommended ΔT (heating) |  | [K] | +20 K | +20 K | +20 K | +20 K | +20 K | +18 K | +12.6 K | +6.3 K | +6.3 K | +4.4 K | +2.2 K | +1.6 K | < +1 K | See note ¹
| Selected Room Temp. @ heating startup |  | [°C] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | -
Recommended Distances & Layout | Max Coverage for Centre Zones (Cmax) |  | [m] | - | - | 34.6 | 26.1 | 23 | 21.2 | 20.1 | 18.3 | 18.1 | 17.7 | 17 | 16.8
| Max Coverage for Perimeter Zones (Cmax) |  | [m] | - | - | 31.4 | 23.6 | 20.8 | 19.1 | 18.1 | 16.4 | 16.3 | 15.9 | 15.3 | 15.1 | 14.8
| Min Coverage (Cmin) |  | [m] | - | - | 10.4 | 8.4 | 7.6 | 7 | 6.7 | 6.2 | 6.1 | 6 | 5.8 | 5.7 | 5.6
| Min Recommended Diffuser Height |  | [m] | 6.4 | 5.2 | 4.5 | 3.9 | 3.7 | 3.6 | 3.5 | 3.5 | 3.5 | 3.5 | 3.6 | 3.7 | 4.1
Comfort | Mean Room Air Velocity |  | [m/s] |  |  | 0.18276 | 0.17282 | 0.16572 | 0.15963 | 0.15496 | 0.1448 | 0.14351 | 0.14088 | 0.13476 | 0.13333 | 0.12974 | Comfort criteria valid for average diffuser spacing of 11.5 m & room temperature of 23 °C (see cells K14 & L23)
| Mean Draught Rating |  | DR |  |  | 18.39% | 17.08% | 16.16% | 15.37% | 14.77% | 13.49% | 13.32% | 12.99% | 12.23% | 12.05% | 11.6%
| Mean PPD |  |  |  |  | 9.286% | 8.728% | 8.344% | 8.024% | 7.785% | 7.281% | 7.219% | 7.093% | 6.805% | 6.738% | 6.574%
| Satifies PPD Category |  | ISO7730 |  |  | B | B | B | B | B | B | B | B | B | B | B
| ¦PMV¦ |  | ISO7730; ASHRAE Std 55 |  |  | ≤ 0.5 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.3 | ≤ 0.3 | ≤ 0.3 | ≤ 0.3 | ≤ 0.3 | ≤ 0.3
T-Element | Thermal Element Setting |  | [°C] | n.r. | n.r. | n.r. | n.r. | n.r. | 30‡ | 30† | 26 | 26 | 24 | 22 | 22 | - | 'n.r.' - thermal element not recommended; consider electric actuator ‡ moderately elevated air velocities in heating † slightly elevated air velocities in heating
Pre-Occupancy Warm-up Boost | Warm-Up Max Boost ΔT |  | [K] | [5 empty] | 18 | 14 | 10.3 | 10.3 | 8.4 | 6.2 | 6
| Warm-Up Airflow Boost Factor | [7 empty] | 1 | 1.05 | 1.28 | 1.28 | 1.38 | 1.67 | 1.95 |  | Thermal Element for Heating When the thermal element is used, the space should always be warmed up from night setback using a supply air temperature greater than or equal to the thermal element setting (row 59), otherwise the guide-ring will retract and prevent heat projection to the floor. Consider introducing a Pre-Occupancy Warm-Up Boost mode (see ‘Notes & Drawings’ rows 12:25).
| Warm-Up Pressure Boost Factor | [7 empty] | 1 | 1.11 | 1.63 | 1.64 | 1.91 | 2.78 | 3.8
| Diffusers Active During Warm-Up Boost |  | % | [5 empty] | 100% | 95% | 78% | 78% | 72% | 60% | 51%
| Recommended Spigot Diameter |  | [mm] | DN250 | DN250 | DN355 | DN355 | DN400 | DN500 | DN500 | DN630 | DN710 | DN710 | DN1000 | DN1000
Product Code & Control Voltage Generator
Select Size & Reducer
|  |  |  | DN250-R1 | DN250-R0 | DN355-R1 | DN355-R0 | DN400-R0 | DN500-R1 | DN500-R0 | DN630-R0 | DN710-R1 | DN710-R0 | DN1000-R1 | DN1000-R0
| Face Shape |  |  | #N/A |  |  | #N/A
| Adjustment Type |  |  | Manual* | 24V Elec. motor 2-10V |  | 24V Elec. motor 2-position |  | 230V Elec. motor 2-position |  | #N/A
| Colour |  |  | RAL9003* (signal white) |  | RAL9005 (jet black) |  | RAL9006 (aluminium) |  | custom colour^
| Accessories |  |  | Diffuser only* |  | With uninsulated connection box |  |  | With mounting bracket (for round duct connection)
|  |  | Order Code | select size to generate order code | [6 empty] | refer to Selection Summary & Print' for a printable summary
|  |  | Product Description | [7 empty] | * indicates standard/default option
^ contact Smartair Diffusion for custom colours
[8 empty] | click to see product on smartair.asia | [10 empty] | Copyright © 2024 SMARTAIR DIFFUSION
Group Box 8
Group Box 45
Group Box 52
Group Box 109
Group Box 347
Group Box 607
Group Box 3959

## Equations HSC-AD (hidden)
Units
| Unit Type | 1 | [L/s] | L/s |  | L/s/m²
| Multiplier | 1
| Alternate | 3.6 | m³/h
Input
Size
| Max airflow rate | 800
| Turndown to | 1
| min flowrate | 800
| max pressure | 60
| diffuser height | 6 | m | [5 empty] | H actual | Height Adjusted | DT old | DT new
| dT cooling | 12 | [6 empty] | 2.7 | 2 | 174.1436 | 317.3766
| Tn.s. | 16 | [6 empty] | 4.5 | 4.5 | 62.6917 | 62.6917
[9 empty] | 3.5 | 3.115 | 103.6332 | 130.8335
| adpi | 90%
| Mean room v | 0.25
| Room Temp Cooling | 23 | C | [5 empty] | 1.389 | -1.75
| room temp checkbox | FALSE
| Room Temp Heating | 21
| dT heating checkbox | FALSE
| dT heating manual input | 4 | K
| adjusted heating height | 6
Thermal Element
| adpi | Tmax correction |  | Min Thermal Setting
| 70% | 0 | 0.2 | 15
| 80% | 2 |  | 17
| 90% | 4 |  | 19
| 95% | 5 |  | 20
| T max Correction | 4 | K | 19
Hmin
| adpi | Hmin factor | Factor
| 70% | 0.9 | 110%
| 80% | 1
| 90% | 1.1
| 95% | 1.15
T max Correction
| Freely Suspended | 2 | free
| Hmin Multiplier | 1.1
| Cmin Multiplier | 0.85
| Cmax Multiplier | 0.8
| Cmin | x = velocity
| H | ax | ^b | Q''
| 2.7 | 4510 | 2.2693 | 194.0536
| 4 | 3884 | 2.2426 | 173.4201
| 10 | 3435 | 2.2754 | 146.5546
| 30 | 2736 | 2.2624 | 118.849
|  | Ax | ^b | Q'' Target
| 6 | 232.5287 | -0.1988 | 162.8476
| v' at Vmax | 13.5706
| v' at Vmin | 17.5706
| correction v' factor | 4
Cmax Table Permiter Zone
| adpi | v' @Vmax | v' @ Vmin |  | Hfactor @ Vmax | Hfactor @ Vmin
| 95% | 0.955 | 1.27 |  | 5.317 | 4.4309
| 90% | 0.75 | 1 |  | 6 | 5
| 85% | 0.60762 | 0.80827 |  | 6.6828 | 5.5685
| 80% | 0.5 | 0.66 |  | 7.3659 | 6.1383
| 70% | 0.35 | 0.47 |  | 8.7318 | 7.2765
| v' & Vmax | 0.75 |  | at ADPI | 6 | factor * room height
| v' & Vmin | 1 |  |  | 5
Cmax-Centre Zone Table
| adpi | v' @Vmax | v' @ Vmin |  | Hfactor @ Vmax | Hfactor @ Vmin
| 95% | 0.75963 | 1.0121 |  | 5.317 | 4.4309
| 90% | 0.60762 | 0.80827 |  | 6 | 5
| 85% | 0.48872 | 0.6503 |  | 6.6828 | 5.5685
| 80% | 0.40294 | 0.53818 |  | 7.3659 | 6.1383
| 70% | 0.33072 | 0.45147 |  | 8.7318 | 7.2765
| v' & Vmax | 0.60762 |  | at ADPI | 6 | factor * room height
| v' & Vmin | 0.80827 |  |  | 5
| Diffuser Distance Selection Type | 1
| Manual Diffuser Distance | 20
| Specific Flow rate | 10 | max | 31
| dist spec flow rate | 8.9443
heating factor
| Low level return | 0% | 1
| Penetration Constant | 4.642
| DN250-R1 |  |  | pressure | V | [5 empty] | DN250-R0 |  |  | pressure | v | [5 empty] | DN355-R1 | [5 empty] | DN355-R0 | [11 empty] | DN400-R0 | [5 empty] | DN500-R1 | [5 empty] | DN500-R0 | [5 empty] | DN630-R1 | [5 empty] | DN630-R0 | [5 empty] | DN710-R1 | [5 empty] | DN710-R0 | [5 empty] | DN1000-R1 | [5 empty] | DN1000-R0 | [5 empty] | DN1340
| Pressure at airflow | 1204.4112 | ptotal-v | 50 | 163 | [5 empty] | Pressure at airflow | 966.0669 | p-v | 50 | 182 | 0.428 |  |  |  |  | Pressure at airflow | 299.264 | p-v | 50 | 327 | 0.79369 | Pressure at airflow | 188.5192 | p-v | 50 | 412 | 0.41 | Pressure at airflow | 186.7021 | p-v | 50 | 414 |  | Pressure at airflow | 128.5135 | p-v | 50 | 499 | 0.41 | Pressure at airflow | 88.0066 | p-v | 50 | 603 | 0.84691 | Pressure at airflow | 63.1233 | p-v | 50 | 712 | 0.41 | Pressure at airflow | 34.9322 | p-v | 50 | 957.11 |  | Pressure at airflow | 25.0607 | p-v | 50 | 1130 | 0.41 | Pressure at airflow | 21.6452 | p-v | 50 | 1215.8892 |  | Pressure at airflow | 15.5252 | p-v | 50 | 1435.6768 |  | Pressure at airflow | 5.5004 | p-v | 50 | 2412 |  | Pressure at airflow | 3.9452 | p-v | 50 | 2848 |  | Pressure at airflow | 1.2236 | p-v | 50 | 5113.8688
|  |  | pstatic | 43.2463 | [8 empty] | pstatic | 41.5801 | [8 empty] | pstatic | 43.3149 |  |  |  |  | pstatic | 39.3878 |  |  |  |  | pstatic | 43.3521 |  |  |  |  | pstatic | 40.342 |  |  |  |  | pstatic | 44.2233 |  |  |  |  | pstatic | 41.9461 |  |  |  |  | pstatic | 44.2259 |  |  |  |  | pstatic | 41.9514 |  |  |  |  | pstatic | 44.2233 |  |  |  |  | pstatic | 41.9461 |  |  |  |  | pstatic | 44.2233 |  |  |  |  | pstatic | 41.9461 |  |  |  |  | pstatic | 41.9461
| Diameter | 209 | [8 empty] | Diameter | 250 | [8 empty] | Diameter | 297 |  |  |  |  | Diameter | 355 |  |  |  |  | Diameter | 335 |  |  |  |  | Diameter | 400 |  |  |  |  | Diameter | 418 |  |  |  |  | Diameter | 500 |  |  |  |  | Diameter | 527 |  |  |  |  | Diameter | 630 |  |  |  |  | Diameter | 594 |  |  |  |  | Diameter | 710 |  |  |  |  | Diameter | 837 |  |  |  |  | Diameter | 1000 |  |  |  |  | Diameter | 1340
| Area | 0.034307 | [8 empty] | Area | 0.049087 | [8 empty] | Area | 0.069279 |  |  |  |  | Area | 0.09898 |  |  |  |  | Area | 0.088141 |  |  |  |  | Area | 0.12566 |  |  |  |  | Area | 0.13723 |  |  |  |  | Area | 0.19635 |  |  |  |  | Area | 0.21813 |  |  |  |  | Area | 0.31172 |  |  |  |  | Area | 0.27712 |  |  |  |  | Area | 0.39592 |  |  |  |  | Area | 0.55023 |  |  |  |  | Area | 0.7854 |  |  |  |  | Area | 1.4103
| Static Pressure | 1041.7266 | [8 empty] | Static Pressure | 803.3824 | [8 empty] | Static Pressure | 259.2518 |  |  |  |  | Static Pressure | 148.5069 |  |  |  |  | Static Pressure | 161.8785 |  |  |  |  | Static Pressure | 103.6899 |  |  |  |  | Static Pressure | 77.8388 |  |  |  |  | Static Pressure | 52.9556 |  |  |  |  | Static Pressure | 30.8982 |  |  |  |  | Static Pressure | 21.0266 |  |  |  |  | Static Pressure | 19.1445 |  |  |  |  | Static Pressure | 13.0244 |  |  |  |  | Static Pressure | 4.8649 |  |  |  |  | Static Pressure | 3.3097 |  |  |  |  | Static Pressure | 1.0265
| Flow at max pressure | 191.9945 | [8 empty] | Flow at max pressure | 218.6273 | [8 empty] | Flow at max pressure | 384.8618 |  |  |  |  | Flow at max pressure | 508.5015 |  |  |  |  | Flow at max pressure | 487.0472 |  |  |  |  | Flow at max pressure | 608.5517 |  |  |  |  | Flow at max pressure | 702.3724 |  |  |  |  | Flow at max pressure | 851.5494 |  |  |  |  | Flow at max pressure | 1114.8062 |  |  |  |  | Flow at max pressure | 1351.3906 |  |  |  |  | Flow at max pressure | 1416.2637 |  |  |  |  | Flow at max pressure | 1717.0641 |  |  |  |  | Flow at max pressure | 2809.4896 |  |  |  |  | Flow at max pressure | 3406.1975 |  |  |  |  | Flow at max pressure | 6116.1682
| Vmin | 69.764 | V at -12K | 69.764 | 12 | [5 empty] | Vmin | 77.896 | V at -12K | 77.896 | 12 | [5 empty] | Vmin | 134.07 | V at -12K | 134.07 | 12 |  | Vmin | 168.92 | V at -12K | 168.92 | 12 |  | Vmin | 172.746 | V at -12K | 172.746 | 12 |  | Vmin | 204.59 | V at -12K | 204.59 | 12 |  | Vmin | 247.23 | V at -12K | 247.23 | 12 |  | Vmin | 291.92 | V at -12K | 291.92 | 12 |  | Vmin | 392.4151 | V at -12K | 392.4151 | 12 |  | Vmin | 463.3 | V at -12K | 463.3 | 12 |  | Vmin | 498.5146 | V at -12K | 498.5146 | 12 |  | Vmin | 588.6275 | V at -12K | 588.6275 | 12 |  | Vmin | 988.92 | V at -12K | 988.92 | 12 |  | Vmin | 1167.68 | V at -12K | 1167.68 | 12 |  | Vmin | 1803.6414 | V at -12K | 2385.9933 | 21
| SWL | 94.469 |  | 14.39 | -7.61 | [5 empty] | SWL | 89.6589 |  | 14.05 | -6.91 | [5 empty] | SWL | 79.3317 |  | 15.63 | -9.78 |  | SWL | 69.3862 |  | 14.24 | -5.22 |  | SWL | 71.5979 |  | 15.332 | -8.581 |  | SWL | 64.0676 |  | 14.256 | -5.16 |  | SWL | 59.7736 |  | 14.67 | -5.91 |  | SWL | 54.2033 |  | 14.29 | -5.03 |  | SWL | 47.3538 |  | 14.459 | -4.025 |  | SWL | 42.9678 |  | 14.319 | -3.158 |  | SWL | 41.1913 |  | 14.328 | -2.8642 |  | SWL | 37.3153 |  | 14.33 | -1.9842 |  | SWL | 24.6117 |  | 14.33 | 0.18153 |  | SWL | 20.7295 |  | 14.33 | 1.0615 |  | SWL | 6.1194 |  | 14.33 | 3.2273
| velocity | 23.3189 | [8 empty] | velocity | 16.2975 | [8 empty] | velocity | 11.5475 |  |  |  |  | velocity | 8.0825 |  |  |  |  | velocity | 9.0763 |  |  |  |  | velocity | 6.3662 |  |  |  |  | velocity | 5.8297 |  |  |  |  | velocity | 4.0744 |  |  |  |  | velocity | 3.6676 |  |  |  |  | velocity | 2.5664 |  |  |  |  | velocity | 2.8869 |  |  |  |  | velocity | 2.0206 |  |  |  |  | velocity | 1.4539 |  |  |  |  | velocity | 1.0186 |  |  |  |  | velocity | 0.56727
| Heating and Thermal Element | [9 empty] | Heating | [9 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating | [5 empty] | Heating
| dT Heating | 144.0116 | [8 empty] | dT Heating | 100.9712 | [8 empty] | dT Heating | 50.1842 |  |  |  |  | dT Heating | 35.2641 |  |  |  |  | dT Heating | 34.9705 |  |  |  |  | dT Heating | 24.6512 |  |  |  |  | dT Heating | 18.0014 |  |  |  |  | dT Heating | 12.6214 |  |  |  |  | dT Heating | 8.9826 |  |  |  |  | dT Heating | 6.3095 |  |  |  |  | dT Heating | 6.273 |  |  |  |  | dT Heating | 4.408 |  |  |  |  | dT Heating | 2.2421 |  |  |  |  | dT Heating | 1.5777 |  |  |  |  | dT Heating | 0.6557 | H |  |  |  | K
| dT Heating low level corrected | 144.0116 | [8 empty] | dT Heating low level corrected | 100.9712 | [8 empty] | dT Heating low level corrected | 50.1842 |  |  |  |  | dT Heating low level corrected | 35.2641 |  |  |  |  | dT Heating low level corrected | 34.9705 |  |  |  |  | dT Heating low level corrected | 24.6512 |  |  |  |  | dT Heating low level corrected | 18.0014 |  |  |  |  | dT Heating low level corrected | 12.6214 |  |  |  |  | dT Heating low level corrected | 8.9826 |  |  |  |  | dT Heating low level corrected | 6.3095 |  |  |  |  | dT Heating low level corrected | 6.273 |  |  |  |  | dT Heating low level corrected | 4.408 |  |  |  |  | dT Heating low level corrected | 2.2421 |  |  |  |  | dT Heating low level corrected | 1.5777 |  |  |  |  | dT Heating low level corrected | 0.6557 | 6 | 4.43e-05 | 1.673 |  | 3.1862
| Thermal element setting raw | 160.0116 | [8 empty] | Thermal element setting raw | 116.9712 | [8 empty] | Thermal element setting raw | 66.1842 |  |  |  |  | Thermal element setting raw | 51.2641 |  |  |  |  | Thermal element setting raw | 50.9705 |  |  |  |  | Thermal element setting raw | 40.6512 |  |  |  |  | Thermal element setting raw | 34.0014 |  |  |  |  | Thermal element setting raw | 28.6214 |  |  |  |  | Thermal element setting raw | 24.9826 |  |  |  |  | Thermal element setting raw | 22.3095 |  |  |  |  | Thermal element setting raw | 22.273 |  |  |  |  | Thermal element setting raw | 20.408 |  |  |  |  | Thermal element setting raw | 18.2421 |  |  |  |  | Thermal element setting raw | 17.5777 |  |  |  |  | Thermal element setting raw | 16.6557
| T s. comfort corrected | 164.0116 | [8 empty] | T s. comfort corrected | 120.9712 | [8 empty] | T s. comfort corrected | 70.1842 |  |  |  |  | T s. comfort corrected | 55.2641 |  |  |  |  | T s. comfort corrected | 54.9705 |  |  |  |  | T s. comfort corrected | 44.6512 |  |  |  |  | T s. comfort corrected | 38.0014 |  |  |  |  | T s. comfort corrected | 32.6214 |  |  |  |  | T s. comfort corrected | 28.9826 |  |  |  |  | T s. comfort corrected | 26.3095 |  |  |  |  | T s. comfort corrected | 26.273 |  |  |  |  | T s. comfort corrected | 24.408 |  |  |  |  | T s. comfort corrected | 22.2421 |  |  |  |  | T s. comfort corrected | 21.5777 |  |  |  |  | T s. comfort corrected | 20.6557
| T.e. setting not rounded | n.r. | [8 empty] | T.e. setting not rounded | n.r. | [8 empty] | T.e. setting not rounded | n.r. |  |  |  |  | T.e. setting not rounded | n.r. |  |  |  |  | T.e. setting not rounded | n.r. |  |  |  |  | T.e. setting not rounded | n.r. |  |  |  |  | T.e. setting not rounded | 30 |  |  |  |  | T.e. setting not rounded | 30 |  |  |  |  | T.e. setting not rounded | 28.9826 |  |  |  |  | T.e. setting not rounded | 26.3095 |  |  |  |  | T.e. setting not rounded | 26.273 |  |  |  |  | T.e. setting not rounded | 24.408 |  |  |  |  | T.e. setting not rounded | 22.2421 |  |  |  |  | T.e. setting not rounded | 22 |  |  |  |  | T.e. setting not rounded | 22
| T element setting | n.r. | [8 empty] | T element setting | n.r. | [8 empty] | T element setting | n.r. |  |  |  |  | T element setting | n.r. |  |  |  |  | T element setting | n.r. |  |  |  |  | T element setting | n.r. |  |  |  |  | T element setting | 30 |  |  |  |  | T element setting | 30 |  |  |  |  | T element setting | 29 |  |  |  |  | T element setting | 26 |  |  |  |  | T element setting | 26 |  |  |  |  | T element setting | 24 |  |  |  |  | T element setting | 22 |  |  |  |  | T element setting | 22 |  |  |  |  | T element setting | 22
| T-element note category | [9 empty] | T-element note category | [9 empty] | T-element note category | [5 empty] | T-element note category | [5 empty] | T-element note category | [5 empty] | T-element note category | [5 empty] | T-element note category | high |  |  |  |  | T-element note category | mid |  |  |  |  | T-element note category | [5 empty] | T-element note category | [5 empty] | T-element note category | [5 empty] | T-element note category | [5 empty] | T-element note category | [5 empty] | T-element note category | [5 empty] | T-element note category
| T- element Note | [9 empty] | T- element Note | [9 empty] | T- element Note | [5 empty] | T- element Note | [5 empty] | T- element Note | [5 empty] | T- element Note | [5 empty] | T- element Note | ‡ |  |  |  |  | T- element Note | † |  |  |  |  | T- element Note | [5 empty] | T- element Note | [5 empty] | T- element Note | [5 empty] | T- element Note | [5 empty] | T- element Note | [5 empty] | T- element Note | [5 empty] | T- element Note
| Warm-up Boost | [9 empty] | Warm-up Boost | [9 empty] | Warm-up Boost | [5 empty] | Warm-up Boost | [5 empty] | Warm-up Boost | [5 empty] | Warm-up Boost | [5 empty] | Warm-up Boost | [5 empty] | Warm-up Boost | [5 empty] | Warm-up Boost | [5 empty] | Warm-up Boost | [5 empty] | Warm-up Boost | [5 empty] | Warm-up Boost | [5 empty] | Warm-up Boost | [5 empty] | Warm-up Boost | [5 empty] | Warm-up Boost
| Warm-up Room to Te setting | #VALUE! | [8 empty] | Warm-up Room to Te setting | #VALUE! | [8 empty] | Warm-up Room to Te setting | #VALUE! |  |  |  |  | Warm-up Room to Te setting | #VALUE! |  |  |  |  | Warm-up Room to Te setting | #VALUE! |  |  |  |  | Warm-up Room to Te setting | #VALUE! |  |  |  |  | Warm-up Room to Te setting | 14 |  |  |  |  | Warm-up Room to Te setting | 14 |  |  |  |  | Warm-up Room to Te setting | 12.9826 |  |  |  |  | Warm-up Room to Te setting | 10.3095 |  |  |  |  | Warm-up Room to Te setting | 10.273 |  |  |  |  | Warm-up Room to Te setting | 8.408 |  |  |  |  | Warm-up Room to Te setting | 6.2421 |  |  |  |  | Warm-up Room to Te setting | 6 |  |  |  |  | Warm-up Room to Te setting | 6
| Actual max DT | 20 | [8 empty] | Actual max DT | 20 | [8 empty] | Actual max DT | 20 |  |  |  |  | Actual max DT | 20 |  |  |  |  | Actual max DT | 20 |  |  |  |  | Actual max DT | 20 |  |  |  |  | Actual max DT | 18.0014 |  |  |  |  | Actual max DT | 12.6214 |  |  |  |  | Actual max DT | 8.9826 |  |  |  |  | Actual max DT | 6.3095 |  |  |  |  | Actual max DT | 6.273 |  |  |  |  | Actual max DT | 4.408 |  |  |  |  | Actual max DT | 2.2421 |  |  |  |  | Actual max DT | 1.5777 |  |  |  |  | Actual max DT | 0.6557
| Choose warmup DT | #VALUE! | [8 empty] | Choose warmup DT | #VALUE! | [8 empty] | Choose warmup DT | #VALUE! |  |  |  |  | Choose warmup DT | #VALUE! |  |  |  |  | Choose warmup DT | #VALUE! |  |  |  |  | Choose warmup DT | #VALUE! |  |  |  |  | Choose warmup DT | 18.0014 |  |  |  |  | Choose warmup DT | 14 |  |  |  |  | Choose warmup DT | 12.9826 |  |  |  |  | Choose warmup DT | 10.3095 |  |  |  |  | Choose warmup DT | 10.273 |  |  |  |  | Choose warmup DT | 8.408 |  |  |  |  | Choose warmup DT | 6.2421 |  |  |  |  | Choose warmup DT | 6 |  |  |  |  | Choose warmup DT | 6
| DT warmup error | [9 empty] | DT warmup error | [9 empty] | DT warmup error | [5 empty] | DT warmup error | [5 empty] | DT warmup error | [5 empty] | DT warmup error | [5 empty] | DT warmup error | 18.0014 |  |  |  |  | DT warmup error | 14 |  |  |  |  | DT warmup error | 12.9826 |  |  |  |  | DT warmup error | 10.3095 |  |  |  |  | DT warmup error | 10.273 |  |  |  |  | DT warmup error | 8.408 |  |  |  |  | DT warmup error | 6.2421 |  |  |  |  | DT warmup error | 6 |  |  |  |  | DT warmup error | 6
| DT % Airflow boost | [9 empty] | DT % Airflow boost | [9 empty] | DT % Airflow boost | [5 empty] | DT % Airflow boost | [5 empty] | DT % Airflow boost | [5 empty] | DT % Airflow boost | [5 empty] | DT % Airflow boost | 1 |  |  |  |  | DT % Airflow boost | 1.0532 |  |  |  |  | DT % Airflow boost | 1.2022 |  |  |  |  | DT % Airflow boost | 1.2783 |  |  |  |  | DT % Airflow boost | 1.2797 |  |  |  |  | DT % Airflow boost | 1.3811 |  |  |  |  | DT % Airflow boost | 1.6685 |  |  |  |  | DT % Airflow boost | 1.9501 |  |  |  |  | DT % Airflow boost | 3.025
| Pressure boost | [9 empty] | Pressure boost | [9 empty] | Pressure boost | [5 empty] | Pressure boost | [5 empty] | Pressure boost | [5 empty] | Pressure boost | [5 empty] | Pressure boost | 1 |  |  |  |  | Pressure boost | 1.1092 |  |  |  |  | Pressure boost | 1.4453 |  |  |  |  | Pressure boost | 1.634 |  |  |  |  | Pressure boost | 1.6377 |  |  |  |  | Pressure boost | 1.9074 |  |  |  |  | Pressure boost | 2.784 |  |  |  |  | Pressure boost | 3.8031 |  |  |  |  | Pressure boost | 9.1506
| % Diffusers Active | [9 empty] | % Diffusers Active | [9 empty] | % Diffusers Active | [5 empty] | % Diffusers Active | [5 empty] | % Diffusers Active | [5 empty] | % Diffusers Active | [5 empty] | % Diffusers Active | 1 |  |  |  |  | % Diffusers Active | 0.94949 |  |  |  |  | % Diffusers Active | 0.8318 |  |  |  |  | % Diffusers Active | 0.78231 |  |  |  |  | % Diffusers Active | 0.78143 |  |  |  |  | % Diffusers Active | 0.72406 |  |  |  |  | % Diffusers Active | 0.59933 |  |  |  |  | % Diffusers Active | 0.51278 |  |  |  |  | % Diffusers Active | 0.33058
| New Min Height | [9 empty] | New Min Height | [9 empty] | New Min Height | [5 empty] | New Min Height | [5 empty] | New Min Height | [5 empty] | New Min Height | [5 empty] | New Min Height | [5 empty] | New Min Height | [5 empty] | New Min Height | [5 empty] | New Min Height | [5 empty] | New Min Height | [5 empty] | New Min Height | [5 empty] | New Min Height | [5 empty] | New Min Height | [5 empty] | New Min Height
| V 100% | 153.7 | [8 empty] | V 100% | 220 | [8 empty] | V 100% | 308 |  |  |  |  | V 100% | 440 |  |  |  |  | V 100% | [5 empty] | V 100% | 563 |  |  |  |  | V 100% | 615 |  |  |  |  | V 100% | 880 |  |  |  |  | V 100% | [5 empty] | V 100% | 1386 |  |  |  |  | V 100% | 1232 |  |  |  |  | V 100% | 1760 |  |  |  |  | V 100% | 2466 |  |  |  |  | V 100% | 3520 |  |  |  |  | V 100% | 6320
| V 50% | 76.85 | [8 empty] | V 50% | 110 | [8 empty] | V 50% | 154 |  |  |  |  | V 50% | 220 |  |  |  |  | V 50% | 0 |  |  |  |  | V 50% | 281.5 |  |  |  |  | V 50% | 307.5 |  |  |  |  | V 50% | 440 |  |  |  |  | V 50% | 0 |  |  |  |  | V 50% | 693 |  |  |  |  | V 50% | 616 |  |  |  |  | V 50% | 880 |  |  |  |  | V 50% | 1233 |  |  |  |  | V 50% | 1760 |  |  |  |  | V 50% | 3160
| Hmin @ 100% | 2.6918 | [8 empty] | Hmin @ 100% | 2.8107 | [8 empty] | Hmin @ 100% | 2.947 |  |  |  |  | Hmin @ 100% | 3.102 |  |  |  |  | Hmin @ 100% | [5 empty] | Hmin @ 100% | 3.255 |  |  |  |  | Hmin @ 100% | 3.3162 |  |  |  |  | Hmin @ 100% | 3.595 |  |  |  |  | Hmin @ 100% | [5 empty] | Hmin @ 100% | 4.037 |  |  |  |  | Hmin @ 100% | 3.9146 |  |  |  |  | Hmin @ 100% | 4.309 |  |  |  |  | Hmin @ 100% | 4.7408 |  |  |  |  | Hmin @ 100% | 5.295 |  |  |  |  | Hmin @ 100% | 6.451
| Ratio below v' 1.0 | 0.91226 | [8 empty] | Ratio below v' 1.0 | 0.90026 | [8 empty] | Ratio below v' 1.0 | 0.88872 |  |  |  |  | Ratio below v' 1.0 | 0.87677 |  |  |  |  | Ratio below v' 1.0 | [5 empty] | Ratio below v' 1.0 | 0.86877 |  |  |  |  | Ratio below v' 1.0 | 0.86582 |  |  |  |  | Ratio below v' 1.0 | 0.85382 |  |  |  |  | Ratio below v' 1.0 | [5 empty] | Ratio below v' 1.0 | 0.83834 |  |  |  |  | Ratio below v' 1.0 | 0.84228 |  |  |  |  | Ratio below v' 1.0 | 0.83033 |  |  |  |  | Ratio below v' 1.0 | 0.8193 |  |  |  |  | Ratio below v' 1.0 | 0.80738 |  |  |  |  | Ratio below v' 1.0 | 0.78777
| Ratio above v' 1.0 | 0.83464 | [8 empty] | Ratio above v' 1.0 | 0.83743 | [8 empty] | Ratio above v' 1.0 | 0.84012 |  |  |  |  | Ratio above v' 1.0 | 0.84291 |  |  |  |  | Ratio above v' 1.0 | [5 empty] | Ratio above v' 1.0 | 0.84477 |  |  |  |  | Ratio above v' 1.0 | 0.84545 |  |  |  |  | Ratio above v' 1.0 | 0.84825 |  |  |  |  | Ratio above v' 1.0 | [5 empty] | Ratio above v' 1.0 | 0.85185 |  |  |  |  | Ratio above v' 1.0 | 0.85094 |  |  |  |  | Ratio above v' 1.0 | 0.85372 |  |  |  |  | Ratio above v' 1.0 | 0.85629 |  |  |  |  | Ratio above v' 1.0 | 0.85906 |  |  |  |  | Ratio above v' 1.0 | 0.86363
| Ratio | 5.2049 | [8 empty] | Ratio | 3.6364 | [8 empty] | Ratio | 2.5974 |  |  |  |  | Ratio | 1.8182 |  |  |  |  | Ratio | #DIV/0! |  |  |  |  | Ratio | 1.421 |  |  |  |  | Ratio | 1.3008 |  |  |  |  | Ratio | 0.90909 |  |  |  |  | Ratio | #DIV/0! |  |  |  |  | Ratio | 0.5772 |  |  |  |  | Ratio | 0.64935 |  |  |  |  | Ratio | 0.45455 |  |  |  |  | Ratio | 0.32441 |  |  |  |  | Ratio | 0.22727 |  |  |  |  | Ratio | 0.12658
|  | Hmin | [9 empty] | Hmin | [9 empty] | Hmin | [5 empty] | Hmin | [5 empty] | Hmin | [5 empty] | Hmin | [5 empty] | Hmin | [5 empty] | Hmin | [5 empty] | Hmin | [5 empty] | Hmin | [5 empty] | Hmin | [5 empty] | Hmin | [5 empty] | Hmin | [5 empty] | Hmin | [5 empty] | Hmin
| <=1.0 | 1.7379 | [8 empty] | <=1.0 | 1.5259 | [8 empty] | <=1.0 | 1.3555 |  |  |  |  | <=1.0 | 1.2017 |  |  |  |  | <=1.0 | #DIV/0! |  |  |  |  | <=1.0 | 1.1105 |  |  |  |  | <=1.0 | 1.0807 |  |  |  |  | <=1.0 | 0.97342 |  |  |  |  | <=1.0 | #DIV/0! |  |  |  |  | <=1.0 | 0.8633 |  |  |  |  | <=1.0 | 0.88939 |  |  |  |  | <=1.0 | 0.8149 |  |  |  |  | <=1.0 | 0.75584 |  |  |  |  | <=1.0 | 0.70232 |  |  |  |  | <=1.0 | 0.62927
| >1 | 2.3907 | [8 empty] | >1 | 1.8572 | [8 empty] | >1 | 1.5108 |  |  |  |  | >1 | 1.2571 |  |  |  |  | >1 | #DIV/0! |  |  |  |  | >1 | 1.1307 |  |  |  |  | >1 | 1.093 |  |  |  |  | >1 | 0.97241 |  |  |  |  | >1 | #DIV/0! |  |  |  |  | >1 | 0.87473 |  |  |  |  | >1 | 0.89546 |  |  |  |  | >1 | 0.84042 |  |  |  |  | >1 | 0.80582 |  |  |  |  | >1 | 0.78219 |  |  |  |  | >1 | 0.76178
| Hmin Select | 6.4352 | [8 empty] | Hmin Select | 5.2199 | [8 empty] | Hmin Select | 4.4523 |  |  |  |  | Hmin Select | 3.8994 |  |  |  |  | Hmin Select | #DIV/0! |  |  |  |  | Hmin Select | 3.6804 |  |  |  |  | Hmin Select | 3.6245 |  |  |  |  | Hmin Select | 3.4995 |  |  |  |  | Hmin Select | #DIV/0! |  |  |  |  | Hmin Select | 3.4851 |  |  |  |  | Hmin Select | 3.4816 |  |  |  |  | Hmin Select | 3.5114 |  |  |  |  | Hmin Select | 3.5833 |  |  |  |  | Hmin Select | 3.7188 |  |  |  |  | Hmin Select | 4.0594
| Min Height | [9 empty] | Min Height | [9 empty] | Min Height | [5 empty] | Min Height | [5 empty] | Min Height | [5 empty] | Min Height | [5 empty] | Min Height | [5 empty] | Min Height | [5 empty] | Min Height | [5 empty] | Min Height | [5 empty] | Min Height | [5 empty] | Min Height | [5 empty] | Min Height | [5 empty] | Min Height | [5 empty] | Min Height
| Hmin | 2.5 | [8 empty] | Hmin | 2.5 | [8 empty] | Hmin | 2.5 |  |  |  |  | Hmin | 2.7 |  |  |  |  | Hmin | 2.7 |  |  |  |  | Hmin | 3 |  |  |  |  | Hmin | 3 |  |  |  |  | Hmin | 3.5 |  |  |  |  | Hmin | 3.5 |  |  |  |  | Hmin | 4 |  |  |  |  | Hmin | 4 |  |  |  |  | Hmin | 4.5 |  |  |  |  | Hmin | 5 |  |  |  |  | Hmin | 5.5 |  |  |  |  | Hmin | 6
| Hmin Flowrate Factor | 1.1 | [8 empty] | Hmin Flowrate Factor | 1.1 | [8 empty] | Hmin Flowrate Factor | 1.1 |  |  |  |  | Hmin Flowrate Factor | 1.1 |  |  |  |  | Hmin Flowrate Factor | 1.1 |  |  |  |  | Hmin Flowrate Factor | 1.1 |  |  |  |  | Hmin Flowrate Factor | 1.0653 |  |  |  |  | Hmin Flowrate Factor | 1.0247 |  |  |  |  | Hmin Flowrate Factor | 0.96717 |  |  |  |  | Hmin Flowrate Factor | 0.94159 |  |  |  |  | Hmin Flowrate Factor | 0.93159 |  |  |  |  | Hmin Flowrate Factor | 0.91145 |  |  |  |  | Hmin Flowrate Factor | 0.9 |  |  |  |  | Hmin Flowrate Factor | 0.9 |  |  |  |  | Hmin Flowrate Factor | 0.9
| Hmin Factor | 3.3275 | [8 empty] | Hmin Factor | 3.3275 | [8 empty] | Hmin Factor | 3.3275 |  |  |  |  | Hmin Factor | 3.5937 |  |  |  |  | Hmin Factor | 3.5937 |  |  |  |  | Hmin Factor | 3.993 |  |  |  |  | Hmin Factor | 3.8672 |  |  |  |  | Hmin Factor | 4.3397 |  |  |  |  | Hmin Factor | 4.096 |  |  |  |  | Hmin Factor | 4.5573 |  |  |  |  | Hmin Factor | 4.5089 |  |  |  |  | Hmin Factor | 4.9628 |  |  |  |  | Hmin Factor | 5.445 |  |  |  |  | Hmin Factor | 5.9895 |  |  |  |  | Hmin Factor | 6.534
| Distance Selection | [9 empty] | Distance Selection | [9 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection
| Vmax | 163 | [8 empty] | Vmax | 182 | [8 empty] | Vmax | 327 |  |  |  |  | Vmax | 412 |  |  |  |  | Vmax | 414 |  |  |  |  | Vmax | 499 |  |  |  |  | Vmax | 603 |  |  |  |  | Vmax | 712 |  |  |  |  | Vmax | 957.11 |  |  |  |  | Vmax | 1130 |  |  |  |  | Vmax | 1215.8892 |  |  |  |  | Vmax | 1435.6768 |  |  |  |  | Vmax | 2412 |  |  |  |  | Vmax | 2848 |  |  |  |  | Vmax | 5113.8688
| Vmin | 48.9 | [8 empty] | Vmin | 54.6 | [8 empty] | Vmin | 98.1 |  |  |  |  | Vmin | 123.6 |  |  |  |  | Vmin | 124.2 |  |  |  |  | Vmin | 149.7 |  |  |  |  | Vmin | 180.9 |  |  |  |  | Vmin | 213.6 |  |  |  |  | Vmin | 287.133 |  |  |  |  | Vmin | 339 |  |  |  |  | Vmin | 364.7668 |  |  |  |  | Vmin | 430.703 |  |  |  |  | Vmin | 723.6 |  |  |  |  | Vmin | 854.4 |  |  |  |  | Vmin | 1534.1606
| Cmin | [9 empty] | Cmin | [9 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin | [5 empty] | Cmin
| v' | -8.7607 | [8 empty] | v' | -5.8328 | [8 empty] | v' | 5.305 |  |  |  |  | v' | 8.1892 |  |  |  |  | v' | 8.2428 |  |  |  |  | v' | 10.1237 |  |  |  |  | v' | 11.7038 |  |  |  |  | v' | 12.8644 |  |  |  |  | v' | 14.5086 |  |  |  |  | v' | 15.2394 |  |  |  |  | v' | 15.5252 |  |  |  |  | v' | 16.1008 |  |  |  |  | v' | 17.3896 |  |  |  |  | v' | 17.6798 |  |  |  |  | v' | 18.391
| Cmin | #NUM! | [8 empty] | Cmin | #NUM! | [8 empty] | Cmin | 12.2801 |  |  |  |  | Cmin | 9.8838 |  |  |  |  | Cmin | 9.8516 |  |  |  |  | Cmin | 8.8894 |  |  |  |  | Cmin | 8.2676 |  |  |  |  | Cmin | 7.8859 |  |  |  |  | Cmin | 7.4256 |  |  |  |  | Cmin | 7.2454 |  |  |  |  | Cmin | 7.1784 |  |  |  |  | Cmin | 7.0489 |  |  |  |  | Cmin | 6.7827 |  |  |  |  | Cmin | 6.7268 |  |  |  |  | Cmin | 6.5954
| Cmin Freely Suspended |  | adjusts for adpi/temp/height through Q vs u_max | [7 empty] | Cmin Freely Suspended |  | adjusts for adpi/temp/height through Q vs u_max | [7 empty] | Cmin Freely Suspended | 10.4381 | adjusts for adpi/temp/height through Q vs u_max |  |  |  | Cmin Freely Suspended | 8.4012 | adjusts for adpi/temp/height through Q vs u_max |  |  |  | Cmin Freely Suspended | 8.3739 | adjusts for adpi/temp/height through Q vs u_max |  |  |  | Cmin Freely Suspended | 7.556 | adjusts for adpi/temp/height through Q vs u_max |  |  |  | Cmin Freely Suspended | 7.0275 | adjusts for adpi/temp/height through Q vs u_max |  |  |  | Cmin Freely Suspended | 6.703 | adjusts for adpi/temp/height through Q vs u_max |  |  |  | Cmin Freely Suspended | 6.3118 | adjusts for adpi/temp/height through Q vs u_max |  |  |  | Cmin Freely Suspended | 6.1586 | adjusts for adpi/temp/height through Q vs u_max |  |  |  | Cmin Freely Suspended | 6.1016 | adjusts for adpi/temp/height through Q vs u_max |  |  |  | Cmin Freely Suspended | 5.9916 | adjusts for adpi/temp/height through Q vs u_max |  |  |  | Cmin Freely Suspended | 5.7653 | adjusts for adpi/temp/height through Q vs u_max |  |  |  | Cmin Freely Suspended | 5.7178 | adjusts for adpi/temp/height through Q vs u_max |  |  |  | Cmin Freely Suspended | 5.6061 | adjusts for adpi/temp/height through Q vs u_max
| Cmax - Perimeter Zone | [9 empty] | Cmax - Perimeter Zone | [9 empty] | Cmax - Perimeter Zone | [5 empty] | Cmax - Perimeter Zone | [5 empty] | Cmax - Perimeter Zone | [5 empty] | Cmax - Perimeter Zone | [5 empty] | Cmax - Perimeter Zone | [5 empty] | Cmax - Perimeter Zone | [5 empty] | Cmax - Perimeter Zone | [5 empty] | Cmax - Perimeter Zone | [5 empty] | Cmax - Perimeter Zone | [5 empty] | Cmax - Perimeter Zone | [5 empty] | Cmax - Perimeter Zone | [5 empty] | Cmax - Perimeter Zone | [5 empty] | Cmax - Perimeter Zone
| v' @ V | -0.64571 | [8 empty] | v' @ V | -0.46272 | [8 empty] | v' @ V | 0.2334 |  |  |  |  | v' @ V | 0.41366 |  |  |  |  | v' @ V | 0.41701 |  |  |  |  | v' @ V | 0.53457 |  |  |  |  | v' @ V | 0.63332 |  |  |  |  | v' @ V | 0.70586 |  |  |  |  | v' @ V | 0.80863 |  |  |  |  | v' @ V | 0.8543 |  |  |  |  | v' @ V | 0.87216 |  |  |  |  | v' @ V | 0.90813 |  |  |  |  | v' @ V | 0.98869 |  |  |  |  | v' @ V | 1.0068 |  |  |  |  | v' @ V | 1.0513
| H Factor | 11.5828 | [8 empty] | H Factor | 10.8509 | [8 empty] | H Factor | 8.0664 |  |  |  |  | H Factor | 7.3454 |  |  |  |  | H Factor | 7.332 |  |  |  |  | H Factor | 6.8617 |  |  |  |  | H Factor | 6.4667 |  |  |  |  | H Factor | 6.1766 |  |  |  |  | H Factor | 5.7655 |  |  |  |  | H Factor | 5.5828 |  |  |  |  | H Factor | 5.5114 |  |  |  |  | H Factor | 5.3675 |  |  |  |  | H Factor | 5.0452 |  |  |  |  | H Factor | 4.9727 |  |  |  |  | H Factor | 4.7949
| c max eqn | #NUM! | [8 empty] | c max eqn | #NUM! | [8 empty] | c max eqn | 39.2737 |  |  |  |  | c max eqn | 29.5005 |  |  |  |  | c max eqn | 29.3817 |  |  |  |  | c max eqn | 25.9507 |  |  |  |  | c max eqn | 23.8418 |  |  |  |  | c max eqn | 22.5836 |  |  |  |  | c max eqn | 21.0998 |  |  |  |  | c max eqn | 20.528 |  |  |  |  | c max eqn | 20.3167 |  |  |  |  | c max eqn | 19.9102 |  |  |  |  | c max eqn | 19.0819 |  |  |  |  | c max eqn | 18.9093 |  |  |  |  | c max eqn | 18.5052
| c max room height | 69.4969 | [8 empty] | c max room height | 65.1052 | [8 empty] | c max room height | 48.3984 |  |  |  |  | c max room height | 44.0721 |  |  |  |  | c max room height | 43.9917 |  |  |  |  | c max room height | 41.1703 |  |  |  |  | c max room height | 38.8003 |  |  |  |  | c max room height | 37.0594 |  |  |  |  | c max room height | 34.593 |  |  |  |  | c max room height | 33.4968 |  |  |  |  | c max room height | 33.0682 |  |  |  |  | c max room height | 32.2048 |  |  |  |  | c max room height | 30.2715 |  |  |  |  | c max room height | 29.8363 |  |  |  |  | c max room height | 28.7695
| Cmax | 55.5975 | final selection | [7 empty] | Cmax | 52.0841 | [8 empty] | Cmax | 31.419 | final selection |  |  |  | Cmax | 23.6004 |  |  |  |  | Cmax | 23.5054 | final selection |  |  |  | Cmax | 20.7606 |  |  |  |  | Cmax | 19.0734 | final selection |  |  |  | Cmax | 18.0668 |  |  |  |  | Cmax | 16.8798 | final selection |  |  |  | Cmax | 16.4224 |  |  |  |  | Cmax | 16.2534 | final selection |  |  |  | Cmax | 15.9282 |  |  |  |  | Cmax | 15.2655 | final selection |  |  |  | Cmax | 15.1274 |  |  |  |  | Cmax | 14.8042
| Cmax - Centre Zone | [9 empty] | Cmax - Centre Zone | [9 empty] | Cmax - Centre Zone | [5 empty] | Cmax - Centre Zone | [5 empty] | Cmax - Centre Zone | [5 empty] | Cmax - Centre Zone | [5 empty] | Cmax - Centre Zone | [5 empty] | Cmax - Centre Zone | [5 empty] | Cmax - Centre Zone | [5 empty] | Cmax - Centre Zone | [5 empty] | Cmax - Centre Zone | [5 empty] | Cmax - Centre Zone | [5 empty] | Cmax - Centre Zone | [5 empty] | Cmax - Centre Zone | [5 empty] | Cmax - Centre Zone
| v' @ V | -0.51262 | [8 empty] | v' @ V | -0.36574 | [8 empty] | v' @ V | 0.19298 |  |  |  |  | v' @ V | 0.33766 |  |  |  |  | v' @ V | 0.34035 |  |  |  |  | v' @ V | 0.43471 |  |  |  |  | v' @ V | 0.51397 |  |  |  |  | v' @ V | 0.57219 |  |  |  |  | v' @ V | 0.65467 |  |  |  |  | v' @ V | 0.69133 |  |  |  |  | v' @ V | 0.70567 |  |  |  |  | v' @ V | 0.73454 |  |  |  |  | v' @ V | 0.7992 |  |  |  |  | v' @ V | 0.81375 |  |  |  |  | v' @ V | 0.84943
| H Factor | 11.5828 | [8 empty] | H Factor | 10.8509 | [8 empty] | H Factor | 8.0664 |  |  |  |  | H Factor | 7.3454 |  |  |  |  | H Factor | 7.332 |  |  |  |  | H Factor | 6.8617 |  |  |  |  | H Factor | 6.4667 |  |  |  |  | H Factor | 6.1766 |  |  |  |  | H Factor | 5.7655 |  |  |  |  | H Factor | 5.5828 |  |  |  |  | H Factor | 5.5114 |  |  |  |  | H Factor | 5.3675 |  |  |  |  | H Factor | 5.0452 |  |  |  |  | H Factor | 4.9727 |  |  |  |  | H Factor | 4.7949
| c max eqn | #NUM! | [8 empty] | c max eqn | #NUM! | [8 empty] | c max eqn | 43.1914 |  |  |  |  | c max eqn | 32.652 |  |  |  |  | c max eqn | 32.5228 |  |  |  |  | c max eqn | 28.7775 |  |  |  |  | c max eqn | 26.4657 |  |  |  |  | c max eqn | 25.0831 |  |  |  |  | c max eqn | 23.4498 |  |  |  |  | c max eqn | 22.8196 |  |  |  |  | c max eqn | 22.5866 |  |  |  |  | c max eqn | 22.1383 |  |  |  |  | c max eqn | 21.2239 |  |  |  |  | c max eqn | 21.0332 |  |  |  |  | c max eqn | 20.5868
| c max room height | 69.4969 | [8 empty] | c max room height | 65.1052 | [8 empty] | c max room height | 48.3984 |  |  |  |  | c max room height | 44.0721 |  |  |  |  | c max room height | 43.9917 |  |  |  |  | c max room height | 41.1703 |  |  |  |  | c max room height | 38.8003 |  |  |  |  | c max room height | 37.0594 |  |  |  |  | c max room height | 34.593 |  |  |  |  | c max room height | 33.4968 |  |  |  |  | c max room height | 33.0682 |  |  |  |  | c max room height | 32.2048 |  |  |  |  | c max room height | 30.2715 |  |  |  |  | c max room height | 29.8363 |  |  |  |  | c max room height | 28.7695
| Cmax | 55.5975 | [8 empty] | Cmax | 52.0841 | [8 empty] | Cmax | 34.5531 |  |  |  |  | Cmax | 26.1216 |  |  |  |  | Cmax | 26.0182 |  |  |  |  | Cmax | 23.022 |  |  |  |  | Cmax | 21.1726 |  |  |  |  | Cmax | 20.0665 |  |  |  |  | Cmax | 18.7599 |  |  |  |  | Cmax | 18.2557 |  |  |  |  | Cmax | 18.0693 |  |  |  |  | Cmax | 17.7106 |  |  |  |  | Cmax | 16.9791 |  |  |  |  | Cmax | 16.8266 |  |  |  |  | Cmax | 16.4694
| Spacing | [9 empty] | Spacing | [9 empty] | Spacing | [5 empty] | Spacing | [5 empty] | Spacing | [5 empty] | Spacing | [5 empty] | Spacing | [5 empty] | Spacing | [5 empty] | Spacing | [5 empty] | Spacing | [5 empty] | Spacing | [5 empty] | Spacing | [5 empty] | Spacing | [5 empty] | Spacing | [5 empty] | Spacing
| Avg Diffuser Distance | 11.4532 | [8 empty] | Avg Diffuser Distance | 11.4532 | [8 empty] | Avg Diffuser Distance | 11.4532 |  |  |  |  | Avg Diffuser Distance | 11.4532 |  |  |  |  | Avg Diffuser Distance | 11.4532 |  |  |  |  | Avg Diffuser Distance | 11.4532 |  |  |  |  | Avg Diffuser Distance | 11.4532 |  |  |  |  | Avg Diffuser Distance | 11.4532 |  |  |  |  | Avg Diffuser Distance | 11.4532 |  |  |  |  | Avg Diffuser Distance | 11.4532 |  |  |  |  | Avg Diffuser Distance | 11.4532 |  |  |  |  | Avg Diffuser Distance | 11.4532 |  |  |  |  | Avg Diffuser Distance | 11.4532 |  |  |  |  | Avg Diffuser Distance | 11.4532 |  |  |  |  | Avg Diffuser Distance | 11.4532
| Dist. From Spec. flowrate | 8.9443 | [8 empty] | Dist. From Spec. flowrate | 8.9443 | [8 empty] | Dist. From Spec. flowrate | 8.9443 |  |  |  |  | Dist. From Spec. flowrate | 8.9443 |  |  |  |  | Dist. From Spec. flowrate | 8.9443 |  |  |  |  | Dist. From Spec. flowrate | 8.9443 |  |  |  |  | Dist. From Spec. flowrate | 8.9443 |  |  |  |  | Dist. From Spec. flowrate | 8.9443 |  |  |  |  | Dist. From Spec. flowrate | 8.9443 |  |  |  |  | Dist. From Spec. flowrate | 8.9443 |  |  |  |  | Dist. From Spec. flowrate | 8.9443 |  |  |  |  | Dist. From Spec. flowrate | 8.9443 |  |  |  |  | Dist. From Spec. flowrate | 8.9443 |  |  |  |  | Dist. From Spec. flowrate | 8.9443 |  |  |  |  | Dist. From Spec. flowrate | 8.9443
| Distance Selected | 11.4532 | [8 empty] | Distance Selected | 11.4532 | [8 empty] | Distance Selected | 11.4532 |  |  |  |  | Distance Selected | 11.4532 |  |  |  |  | Distance Selected | 11.4532 |  |  |  |  | Distance Selected | 11.4532 |  |  |  |  | Distance Selected | 11.4532 |  |  |  |  | Distance Selected | 11.4532 |  |  |  |  | Distance Selected | 11.4532 |  |  |  |  | Distance Selected | 11.4532 |  |  |  |  | Distance Selected | 11.4532 |  |  |  |  | Distance Selected | 11.4532 |  |  |  |  | Distance Selected | 11.4532 |  |  |  |  | Distance Selected | 11.4532 |  |  |  |  | Distance Selected | 11.4532
| Area | 131.1757 | [8 empty] | Area | 131.1757 | [8 empty] | Area | 131.1757 |  |  |  |  | Area | 131.1757 |  |  |  |  | Area | 131.1757 |  |  |  |  | Area | 131.1757 |  |  |  |  | Area | 131.1757 |  |  |  |  | Area | 131.1757 |  |  |  |  | Area | 131.1757 |  |  |  |  | Area | 131.1757 |  |  |  |  | Area | 131.1757 |  |  |  |  | Area | 131.1757 |  |  |  |  | Area | 131.1757 |  |  |  |  | Area | 131.1757 |  |  |  |  | Area | 131.1757
| V" | 6.0987 | [8 empty] | V" | 6.0987 | [8 empty] | V" | 6.0987 |  |  |  |  | V" | 6.0987 |  |  |  |  | V" | 6.0987 |  |  |  |  | V" | 6.0987 |  |  |  |  | V" | 6.0987 |  |  |  |  | V" | 6.0987 |  |  |  |  | V" | 6.0987 |  |  |  |  | V" | 6.0987 |  |  |  |  | V" | 6.0987 |  |  |  |  | V" | 6.0987 |  |  |  |  | V" | 6.0987 |  |  |  |  | V" | 6.0987 |  |  |  |  | V" | 6.0987
| Q" | 73.1843 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity | [6 empty] | Q" | 73.1843 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity | [6 empty] | Q" | 73.1843 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity |  |  | Q" | 73.1843 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity |  |  | Q" | 73.1843 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity |  |  | Q" | 73.1843 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity |  |  | Q" | 73.1843 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity |  |  | Q" | 73.1843 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity |  |  | Q" | 73.1843 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity |  |  | Q" | 73.1843 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity |  |  | Q" | 73.1843 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity |  |  | Q" | 73.1843 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity |  |  | Q" | 73.1843 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity |  |  | Q" | 73.1843 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity |  |  | Q" | 73.1843 | W/m2 | note: Q*1.2 density ignored to compensate for mean velocity to max velocity
| V'' correction factor | -8.512 | [8 empty] | V'' correction factor | -7.396 | [8 empty] | V'' correction factor | -3.1506 |  |  |  |  | V'' correction factor | -2.0512 |  |  |  |  | V'' correction factor | -2.0308 |  |  |  |  | V'' correction factor | -1.3138 |  |  |  |  | V'' correction factor | -0.71159 |  |  |  |  | V'' correction factor | -0.2692 |  |  |  |  | V'' correction factor | 0.35754 |  |  |  |  | V'' correction factor | 0.63608 |  |  |  |  | V'' correction factor | 0.74501 |  |  |  |  | V'' correction factor | 0.9644 |  |  |  |  | V'' correction factor | 1.4557 |  |  |  |  | V'' correction factor | 1.5663 |  |  |  |  | V'' correction factor | 1.8374
| V'' corrected | 14.6107 | [8 empty] | V'' corrected | 13.4947 | [8 empty] | V'' corrected | 9.2493 |  |  |  |  | V'' corrected | 8.1499 |  |  |  |  | V'' corrected | 8.1295 |  |  |  |  | V'' corrected | 7.4125 |  |  |  |  | V'' corrected | 6.8103 |  |  |  |  | V'' corrected | 6.3679 |  |  |  |  | V'' corrected | 5.7412 |  |  |  |  | V'' corrected | 5.4626 |  |  |  |  | V'' corrected | 5.3537 |  |  |  |  | V'' corrected | 5.1343 |  |  |  |  | V'' corrected | 4.643 |  |  |  |  | V'' corrected | 4.5324 |  |  |  |  | V'' corrected | 4.2613
| Q'' adjusted | 126.6745 | [8 empty] | Q'' adjusted | 116.9988 | [8 empty] | Q'' adjusted | 80.1913 |  |  |  |  | Q'' adjusted | 70.6597 |  |  |  |  | Q'' adjusted | 70.4826 |  |  |  |  | Q'' adjusted | 64.2667 |  |  |  |  | Q'' adjusted | 59.0451 |  |  |  |  | Q'' adjusted | 55.2096 |  |  |  |  | Q'' adjusted | 49.7758 |  |  |  |  | Q'' adjusted | 47.3608 |  |  |  |  | Q'' adjusted | 46.4164 |  |  |  |  | Q'' adjusted | 44.5143 |  |  |  |  | Q'' adjusted | 40.2549 |  |  |  |  | Q'' adjusted | 39.296 |  |  |  |  | Q'' adjusted | 36.9457
| V | 2.7 | 0.024532 | 0.44066 | 0.20716 | [5 empty] | V | 2.7 | 0.024532 | 0.44066 | 0.20003 | [5 empty] | V | 2.7 | 0.024532 | 0.44066 | 0.16936 |  | V | 2.7 | 0.024532 | 0.44066 | 0.16017 |  | V | 2.7 | 0.024532 | 0.44066 | 0.16 |  | V | 2.7 | 0.024532 | 0.44066 | 0.15362 |  | V | 2.7 | 0.024532 | 0.44066 | 0.14799 |  | V | 2.7 | 0.024532 | 0.44066 | 0.14367 |  | V | 2.7 | 0.024532 | 0.44066 | 0.13726 |  | V | 2.7 | 0.024532 | 0.44066 | 0.13428 |  | V | 2.7 | 0.024532 | 0.44066 | 0.1331 |  | V | 2.7 | 0.024532 | 0.44066 | 0.13067 |  | V | 2.7 | 0.024532 | 0.44066 | 0.125 |  | V | 2.7 | 0.024532 | 0.44066 | 0.12368 |  | V | 2.7 | 0.024532 | 0.44066 | 0.12036
|  | 4 | 0.02509 | 0.44591 | 0.21733 | [6 empty] | 4 | 0.02509 | 0.44591 | 0.20976 | [6 empty] | 4 | 0.02509 | 0.44591 | 0.17724 |  |  | 4 | 0.02509 | 0.44591 | 0.16752 |  |  | 4 | 0.02509 | 0.44591 | 0.16733 |  |  | 4 | 0.02509 | 0.44591 | 0.16058 |  |  | 4 | 0.02509 | 0.44591 | 0.15463 |  |  | 4 | 0.02509 | 0.44591 | 0.15007 |  |  | 4 | 0.02509 | 0.44591 | 0.14329 |  |  | 4 | 0.02509 | 0.44591 | 0.14015 |  |  | 4 | 0.02509 | 0.44591 | 0.13889 |  |  | 4 | 0.02509 | 0.44591 | 0.13633 |  |  | 4 | 0.02509 | 0.44591 | 0.13035 |  |  | 4 | 0.02509 | 0.44591 | 0.12895 |  |  | 4 | 0.02509 | 0.44591 | 0.12546
|  | 10 | 0.027927 | 0.43948 | 0.23448 | [6 empty] | 10 | 0.027927 | 0.43948 | 0.22644 | [6 empty] | 10 | 0.027927 | 0.43948 | 0.1918 |  |  | 10 | 0.027927 | 0.43948 | 0.18143 |  |  | 10 | 0.027927 | 0.43948 | 0.18123 |  |  | 10 | 0.027927 | 0.43948 | 0.17402 |  |  | 10 | 0.027927 | 0.43948 | 0.16766 |  |  | 10 | 0.027927 | 0.43948 | 0.16278 |  |  | 10 | 0.027927 | 0.43948 | 0.15554 |  |  | 10 | 0.027927 | 0.43948 | 0.15217 |  |  | 10 | 0.027927 | 0.43948 | 0.15083 |  |  | 10 | 0.027927 | 0.43948 | 0.14808 |  |  | 10 | 0.027927 | 0.43948 | 0.14168 |  |  | 10 | 0.027927 | 0.43948 | 0.14019 |  |  | 10 | 0.027927 | 0.43948 | 0.13644
|  | 30 | 0.030254 | 0.442 | 0.25714 | [6 empty] | 30 | 0.030254 | 0.442 | 0.24827 | [6 empty] | 30 | 0.030254 | 0.442 | 0.21009 |  |  | 30 | 0.030254 | 0.442 | 0.19866 |  |  | 30 | 0.030254 | 0.442 | 0.19844 |  |  | 30 | 0.030254 | 0.442 | 0.19051 |  |  | 30 | 0.030254 | 0.442 | 0.1835 |  |  | 30 | 0.030254 | 0.442 | 0.17814 |  |  | 30 | 0.030254 | 0.442 | 0.17016 |  |  | 30 | 0.030254 | 0.442 | 0.16646 |  |  | 30 | 0.030254 | 0.442 | 0.16499 |  |  | 30 | 0.030254 | 0.442 | 0.16196 |  |  | 30 | 0.030254 | 0.442 | 0.15492 |  |  | 30 | 0.030254 | 0.442 | 0.15328 |  |  | 30 | 0.030254 | 0.442 | 0.14916
| Room Height |  | Ax | ^b |  | m/s |  |  |  |  | Room Height |  | Ax | ^b |  | m/s |  |  |  |  | Room Height |  | Ax | ^b |  | m/s | Room Height |  | Ax | ^b |  | m/s | Room Height |  | Ax | ^b |  | m/s | Room Height |  | Ax | ^b |  | m/s | Room Height |  | Ax | ^b |  | m/s | Room Height |  | Ax | ^b |  | m/s | Room Height |  | Ax | ^b |  | m/s | Room Height |  | Ax | ^b |  | m/s | Room Height |  | Ax | ^b |  | m/s | Room Height |  | Ax | ^b |  | m/s | Room Height |  | Ax | ^b |  | m/s | Room Height |  | Ax | ^b |  | m/s | Room Height |  | Ax | ^b |  | m/s
|  | 6 | 0.19109 | 0.087955 | 0.2237 | [6 empty] | 6 | 0.18448 | 0.087996 | 0.21598 | [6 empty] | 6 | 0.15605 | 0.088195 | 0.18276 |  |  | 6 | 0.14754 | 0.088262 | 0.17282 |  |  | 6 | 0.14737 | 0.088263 | 0.17263 |  |  | 6 | 0.14147 | 0.088312 | 0.16572 |  |  | 6 | 0.13625 | 0.088357 | 0.15963 |  |  | 6 | 0.13226 | 0.088392 | 0.15496 |  |  | 6 | 0.12633 | 0.088447 | 0.14802 |  |  | 6 | 0.12357 | 0.088473 | 0.1448 |  |  | 6 | 0.12247 | 0.088484 | 0.14351 |  |  | 6 | 0.12022 | 0.088506 | 0.14088 |  |  | 6 | 0.11498 | 0.088559 | 0.13476 |  |  | 6 | 0.11376 | 0.088571 | 0.13333 |  |  | 6 | 0.1107 | 0.088604 | 0.12974
| DR | 23.97% | [8 empty] | DR | 22.89% | [8 empty] | DR | 18.39% |  |  |  |  | DR | 17.08% |  |  |  |  | DR | 17.05% |  |  |  |  | DR | 16.16% |  |  |  |  | DR | 15.37% |  |  |  |  | DR | 14.77% |  |  |  |  | DR | 13.89% |  |  |  |  | DR | 13.49% |  |  |  |  | DR | 13.32% |  |  |  |  | DR | 12.99% |  |  |  |  | DR | 12.23% |  |  |  |  | DR | 12.05% |  |  |  |  | DR | 11.6%
| PPD | 11.87% | [8 empty] | PPD | 11.34% | [8 empty] | PPD | 9.286% |  |  |  |  | PPD | 8.728% |  |  |  |  | PPD | 8.717% |  |  |  |  | PPD | 8.344% |  |  |  |  | PPD | 8.024% |  |  |  |  | PPD | 7.785% |  |  |  |  | PPD | 7.438% |  |  |  |  | PPD | 7.281% |  |  |  |  | PPD | 7.219% |  |  |  |  | PPD | 7.093% |  |  |  |  | PPD | 6.805% |  |  |  |  | PPD | 6.738% |  |  |  |  | PPD | 6.574%
| ISO category | C | [8 empty] | ISO category | C | [8 empty] | ISO category | B |  |  |  |  | ISO category | B |  |  |  |  | ISO category | B |  |  |  |  | ISO category | B |  |  |  |  | ISO category | B |  |  |  |  | ISO category | B |  |  |  |  | ISO category | B |  |  |  |  | ISO category | B |  |  |  |  | ISO category | B |  |  |  |  | ISO category | B |  |  |  |  | ISO category | B |  |  |  |  | ISO category | B |  |  |  |  | ISO category | B
| PMV | 0.5921 | [8 empty] | PMV | 0.57125 | [8 empty] | PMV | 0.472 |  |  |  |  | PMV | 0.4386 |  |  |  |  | PMV | 0.43794 |  |  |  |  | PMV | 0.41348 |  |  |  |  | PMV | 0.39093 |  |  |  |  | PMV | 0.37299 |  |  |  |  | PMV | 0.34515 |  |  |  |  | PMV | 0.33172 |  |  |  |  | PMV | 0.32626 |  |  |  |  | PMV | 0.31489 |  |  |  |  | PMV | 0.28737 |  |  |  |  | PMV | 0.28073 |  |  |  |  | PMV | 0.26366
| V'' Result | 6.0987 | L/s | [7 empty] | V'' Result | 6.0987 | [8 empty] | V'' Result | 6.0987 |  |  |  |  | V'' Result | 6.0987 |  |  |  |  | V'' Result | 6.0987 |  |  |  |  | V'' Result | 6.0987 |  |  |  |  | V'' Result | 6.0987 |  |  |  |  | V'' Result | 6.0987 |  |  |  |  | V'' Result | 6.0987 |  |  |  |  | V'' Result | 6.0987 |  |  |  |  | V'' Result | 6.0987 |  |  |  |  | V'' Result | 6.0987 |  |  |  |  | V'' Result | 6.0987 |  |  |  |  | V'' Result | 6.0987 |  |  |  |  | V'' Result | 6.0987
| Distance Result | 11.4532 | [8 empty] | Distance Result | 11.4532 | [8 empty] | Distance Result | 11.4532 |  |  |  |  | Distance Result | 11.4532 |  |  |  |  | Distance Result | 11.4532 |  |  |  |  | Distance Result | 11.4532 |  |  |  |  | Distance Result | 11.4532 |  |  |  |  | Distance Result | 11.4532 |  |  |  |  | Distance Result | 11.4532 |  |  |  |  | Distance Result | 11.4532 |  |  |  |  | Distance Result | 11.4532 |  |  |  |  | Distance Result | 11.4532 |  |  |  |  | Distance Result | 11.4532 |  |  |  |  | Distance Result | 11.4532 |  |  |  |  | Distance Result | 11.4532
| V'' Result Unit_edit | 6.0987 | L/s/m²
| Average Dist | DN250 R1 | DN250 | DN355 R1 | DN355 | DN400 | DN500 R1 | DN500 | DN630 | DN710 R1 | DN710 | DN1000 R1 | DN1000 | DN1340
| Cmax - Perimeter | 55.5975 | 52.0841 | 31.419 | 23.6004 | 20.7606 | 19.0734 | 18.0668 | 16.4224 | 16.2534 | 15.9282 | 15.2655 | 15.1274 | 14.8042
| Cmin |  |  | 10.4381 | 8.4012 | 7.556 | 7.0275 | 6.703 | 6.1586 | 6.1016 | 5.9916 | 5.7653 | 5.7178 | 5.6061
| ACCEPT | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE
| Cmax | [6 empty] | 18.0668 | 16.4224 | 16.2534 | 15.9282
| Cmin | [6 empty] | 6.703 | 6.1586 | 6.1016 | 5.9916
| IF ALL NUMBERS FAILED | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
| Cmax |  |  | 31.419 | 23.6004 | 20.7606 | 19.0734 | 18.0668 | 16.4224 | 16.2534 | 15.9282 | 15.2655 | 15.1274 | 14.8042
| Cmin |  |  | 10.4381 | 8.4012 | 7.556 | 7.0275 | 6.703 | 6.1586 | 6.1016 | 5.9916 | 5.7653 | 5.7178 | 5.6061
| Average | 11.4532 | m
| Results | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
|  | DN250 R1 | DN250 | DN355 R1 | DN355 | DN400 | DN500 R1 | DN500 | DN630 | DN710 R1 | DN710 | DN1000 R1 | DN1000 | DN1340
| Max Airflow | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800
| Airflow @ Max Pressure | 191.9945 | 218.6273 | 384.8618 | 508.5015 | 608.5517 | 702.3724 | 851.5494 | 1351.3906 | 1416.2637 | 1717.0641 | 2809.4896 | 3406.1975 | 6116.1682
| Min Airflow | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800
| Min Permissible Airflow | 69.764 | 77.896 | 134.07 | 168.92 | 204.59 | 247.23 | 291.92 | 463.3 | 498.5146 | 588.6275 | 988.92 | 1167.68 | 1803.6414
| Static Pressure | 1041.7266 | 803.3824 | 259.2518 | 148.5069 | 103.6899 | 77.8388 | 52.9556 | 21.0266 | 19.1445 | 13.0244 | 4.8649 | 3.3097 | 1.0265
| Total Pressure | 1204.4112 | 966.0669 | 299.264 | 188.5192 | 128.5135 | 88.0066 | 63.1233 | 25.0607 | 21.6452 | 15.5252 | 5.5004 | 3.9452 | 1.2236
| Max Permissible P | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Sound Power Level | 94.469 | 89.6589 | 79.3317 | 69.3862 | 64.0676 | 59.7736 | 54.2033 | 42.9678 | 41.1913 | 37.3153 | 24.6117 | 20.7295 | 6.1194
| ΔT_max (heating) | 144.0116 | 100.9712 | 50.1842 | 35.2641 | 24.6512 | 18.0014 | 12.6214 | 6.3095 | 6.273 | 4.408 | 2.2421 | 1.5777 | 0.6557
| Guide ring mm | 13.3 | 13.3 | 18.6 | 14.88 | 14.56 | 16.9 | 13 | 6.56 | 7.3 | 1.825 | -15.3 | -22.95 | -47.81
| T n.s. | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
| Hmin | 6.4352 | 5.2199 | 4.4523 | 3.8994 | 3.6804 | 3.6245 | 3.4995 | 3.4851 | 3.4816 | 3.5114 | 3.5833 | 3.7188 | 4.0594
| Cmax - Centre | 55.5975 | 52.0841 | 34.5531 | 26.1216 | 23.022 | 21.1726 | 20.0665 | 18.2557 | 18.0693 | 17.7106 | 16.9791 | 16.8266 | 16.4694
| Cmax - Perimeter | 55.5975 | 52.0841 | 31.419 | 23.6004 | 20.7606 | 19.0734 | 18.0668 | 16.4224 | 16.2534 | 15.9282 | 15.2655 | 15.1274 | 14.8042
| Cmin |  |  | 10.4381 | 8.4012 | 7.556 | 7.0275 | 6.703 | 6.1586 | 6.1016 | 5.9916 | 5.7653 | 5.7178 | 5.6061
| Mean Air Velocity | 0.2237 | 0.21598 | 0.18276 | 0.17282 | 0.16572 | 0.15963 | 0.15496 | 0.1448 | 0.14351 | 0.14088 | 0.13476 | 0.13333 | 0.12974
| Draft Rating | 23.97% | 22.89% | 18.39% | 17.08% | 16.16% | 15.37% | 14.77% | 13.49% | 13.32% | 12.99% | 12.23% | 12.05% | 11.6%
| PPD | 11.87% | 11.34% | 9.286% | 8.728% | 8.344% | 8.024% | 7.785% | 7.281% | 7.219% | 7.093% | 6.805% | 6.738% | 6.574%
| PMV | C | C | B | B | B | B | B | B | B | B | B | B | B
| PPD Class | 59.21% | 57.12% | 47.2% | 43.86% | 41.35% | 39.09% | 37.3% | 33.17% | 32.63% | 31.49% | 28.74% | 28.07% | 26.37%
| T.s-note | [5 empty] | ‡ | †
| T s. | n.r. | n.r. | n.r. | n.r. | n.r. | 30 | 30 | 26 | 26 | 24 | 22 | 22 | -
| warm-up dt | [5 empty] | 18.0014 | 14 | 10.3095 | 10.273 | 8.408 | 6.2421 | 6 | 6
| warm-up airflow boost | [5 empty] | 1 | 1.0532 | 1.2783 | 1.2797 | 1.3811 | 1.6685 | 1.9501 | 3.025
| pressure airflow boost | [5 empty] | 1 | 1.1092 | 1.634 | 1.6377 | 1.9074 | 2.784 | 3.8031 | 9.1506
| Diffuser shut off % | [5 empty] | 1 | 0.94949 | 0.78231 | 0.78143 | 0.72406 | 0.59933 | 0.51278 | 0.33058
|  | 209.165 | 250 | 297.0143 | 355 | 400 | 418.33 | 500 | 630 | 594.0286 | 710 | 836.66 | 1000 | 1340 |  |  | 209.165 | 250 | 297.0143 | 355 | 418.33 | 500 | 594.0286 | 710 | 836.66 | 1000
| Stroke | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
| ΔT_max (heating) | 20 | 20 | 20 | 20 | 20 | 18.0014 | 12.6214 | 6.3095 | 6.273 | 4.408 | 2.2421 | 1.5777 | < +1 K
| Guide Ring mm | 13.3 | 13.3 | 18.6 | 14.88 | 14.56 | 16.9 | 13 | 6.56 | 7.3 | 1.825 | 2.2421 | 1.5777 | < +1 K
| T n.s. | +18 | +18 | +18 | +18 | +18 | +18 | 12.6214 | 6.3095 | 6.273 | 4.408 | 2.2421 | 1.5777 | < +1
| Guide Ring mm | 13.3 | 13.3 | 18.6 | 14.88 | 14.56 | 16.9 | 13 | 6.56 | 7.3 | 1.825 | 2.2421 | 1.5777 | < +1
| display | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | True = mm
| ΔT_max (heating) | +20 K | +20 K | +20 K | +20 K | +20 K | +18 K | +12.6 K | +6.3 K | +6.3 K | +4.4 K | +2.2 K | +1.6 K | < +1 K
| Guide ring mm | 13 mm | 13 mm | 19 mm | 15 mm | 15 mm | 17 mm | 13 mm | 7 mm | 7 mm | 2 mm | -15 mm | -23 mm | -48 mm
| Select | +20 K | +20 K | +20 K | +20 K | +20 K | +18 K | +12.6 K | +6.3 K | +6.3 K | +4.4 K | +2.2 K | +1.6 K | < +1 K
[17 empty] | 140.0116 | 96.9712 | 46.1842 | 31.2641 | 14.0014 | 8.6214 | 2.273 | 0.40801 | -1.7579 | -2.4223
1 | Result Validation | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 0
2 |  | DN250 R1 | DN250 | DN355 R1 | DN355 | DN400 | DN500 R1 | DN500 | DN630 | DN710 R1 | DN710 | DN1000 R1 | DN1000 | DN1340
3 | Max Airflow [L/s] | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800
4 | Airflow @ Max Pressure [L/s] | 191.9945 | 218.6273 | 384.8618 | 508.5015 | 608.5517 | 702.3724 | 851.5494 | 1351.3906 | 1416.2637 | 1717.0641 | 2809.4896 | 3406.1975 | 6116.1682
5 | Min Airflow (Turndown To) [L/s] | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800
6 | Min Permissible Airflow [L/s] | 69.764 | 77.896 | 134.07 | 168.92 | 204.59 | 247.23 | 291.92 | 463.3 | 498.5146 | 588.6275 | 988.92 | 1167.68 | 1803.6414
7 | Static Pressure | 1041.7266 | 803.3824 | 259.2518 | 148.5069 | 103.6899 | 77.8388 | 52.9556 | 21.0266 | 19.1445 | 13.0244 | 4.8649 | < 5 | < 5
8 | Total Pressure | 1204.4112 | 966.0669 | 299.264 | 188.5192 | 128.5135 | 88.0066 | 63.1233 | 25.0607 | 21.6452 | 15.5252 | < 10 | < 10 | < 10
9 | Max Permissible P | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
10 | Sound Power Level | 94.469 | 89.6589 | 79.3317 | 69.3862 | 64.0676 | 59.7736 | 54.2033 | 42.9678 | 41.1913 | 37.3153 | 24.6117 | 20.7295 | < 20
11 | ΔT_max (heating) | +20 K | +20 K | +20 K | +20 K | +20 K | +18 K | +12.6 K | +6.3 K | +6.3 K | +4.4 K | +2.2 K | +1.6 K | < +1 K
12 | T n.s. | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | -
13 | Cmax - Centre | - | - | 34.6 | 26.1 | 23 | 21.2 | 20.1 | 18.3 | 18.1 | 17.7 | 17 | 16.8 | 16.5
14 | Cmax - Perimeter | - | - | 31.4 | 23.6 | 20.8 | 19.1 | 18.1 | 16.4 | 16.3 | 15.9 | 15.3 | 15.1 | 14.8
15 | Cmin | - | - | 10.4 | 8.4 | 7.6 | 7 | 6.7 | 6.2 | 6.1 | 6 | 5.8 | 5.7 | 5.6
16 | Hmin | 6.4 | 5.2 | 4.5 | 3.9 | 3.7 | 3.6 | 3.5 | 3.5 | 3.5 | 3.5 | 3.6 | 3.7 | 4.1
17 | Mean Air Velocity |  |  | 0.18276 | 0.17282 | 0.16572 | 0.15963 | 0.15496 | 0.1448 | 0.14351 | 0.14088 | 0.13476 | 0.13333 | 0.12974
18 | Draft Rating |  |  | 18.39% | 17.08% | 16.16% | 15.37% | 14.77% | 13.49% | 13.32% | 12.99% | 12.23% | 12.05% | 11.6%
19 | PPD |  |  | 9.286% | 8.728% | 8.344% | 8.024% | 7.785% | 7.281% | 7.219% | 7.093% | 6.805% | 6.738% | 6.574%
20 | PPD Class | bar: 3 to 13
21 | PMV |  |  | ≤ 0.5 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.3 | ≤ 0.3 | ≤ 0.3 | ≤ 0.3 | ≤ 0.3 | ≤ 0.3
22 | T s. | n.r. | n.r. | n.r. | n.r. | n.r. | 30‡ | 30† | 26 | 26 | 24 | 22 | 22 | -
23 | Warm-up DT | 6: 18; 7: 14; 8: 10.3; 9: 10.3; 10: 8.4; 11: 6.2; 12: 6; 13: 6
24 | Warm-Up Airflow Boost | 6: 1; 7: 1.05; 8: 1.28; 9: 1.28; 10: 1.38; 11: 1.67; 12: 1.95; 13: 3.02
25 | Warm-Up Pressure Boost | 6: 1; 7: 1.11; 8: 1.63; 9: 1.64; 10: 1.91; 11: 2.78; 12: 3.8; 13: 9.15
26 | Diffuser shut off % | 6: 1; 7: 0.95; 8: 0.78; 9: 0.78; 10: 0.72; 11: 0.6; 12: 0.51; 13: 0.33
27 | ΔT_max (heating) | +18 | +18 | +18 | +18 | +18 | +18 | 12.6214 | 6.3095 | 6.273 | 4.408 | 2.2421 | 1.5777 | < +1
28 | Recommended Spigot Dia. | DN250 | DN250 | DN355 | DN355 | DN400 | DN500 | DN500 | DN630 | DN710 | DN710 | DN1000 | DN1000
29 | T-setting Number | n.r. | n.r. | n.r. | n.r. | n.r. | 30 | 30 | 26 | 26 | 24 | 22 | 22 | -
30 | T-Setting Note | 6: ‡; 7: †; 13: 0
31 | T-setting Category | 6: high; 7: mid
Highlighting Rules
|  | DN250 R1 | DN250 | DN355 R1 | DN355 | DN400 | DN500 R1 | DN500 | DN630 | DN710 R1 | DN710 | DN1000 R1 | DN1000 | DN1340 | Combine boolean up to DN1000
| Max Airflow | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE |  | true = shade
| Min Airflow | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE |  | true = shade
| Static Pressure not number | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
| Total Pressure not number | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE
| Max Permissible dT | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | true = red
| cmax - centre | #VALUE! | #VALUE! | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
| cmax - perimeter | #VALUE! | #VALUE! | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
| cmin | #VALUE! | #VALUE! | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
| hmin | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
| thermal element | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE |  | TRUE | true = red
| airfow-shade | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE |  | true = shade
| Unshaded Number | 7: 7; 8: 8; 9: 9; 10: 10
|  |  | dT heating | [8 empty] | Model |  |  | mm (100%)
| Model Selection | 1: 0; 11: 1; 12: DN250-R1; 13: 144.0116; 0: 13.3
| Default Selection | 1: 7; 2: 12.6214; 11: 2; 12: DN250-R0; 13: 100.9712; 0: 13.3
| Controls | 1: Left; 7: Chart Tick Marks; 11: 3; 12: DN355-R1; 13: 50.1842; 0: 18.6
|  | V | T |  |  | mm |  | 0 | 0 mm |  |  | 4 | DN355-R0 | 35.2641 | 18.6
|  | 10 | -6 |  | 0% | 26 |  | 25% | 7 mm |  |  | 5 | DN400-R0 | 24.6512 | 20.8
|  | 2 | 25.2428 |  | 100% | 0 |  | 0.5 | 13 mm |  |  | 6 | DN500-R1 | 18.0014 | 26
[8 empty] | 75% | 20 mm |  |  | 7 | DN500-R0 | 12.6214 | 26
|  | dT | V |  | %x | mm |  | 1 | 26 mm |  |  | 8 | DN630-R0 | 6.3095 | 32.8
|  | -12 | 10 |  | 0% | 26 | [5 empty] | 9 | DN710-R1 | 6.273 | 36.5
|  | -6 | 10 |  | 19.2% | 21.0068 | mm |  |  |  |  | 10 | DN710-R0 | 4.408 | 36.5
|  | 0 | 8.4636 | 8.5 V | 59.6% | 10.5034 | mm |  |  |  |  | 11 | DN1000-R1 | 2.2421 | 51
| Right | 1: 12.6214; 2: 2; 4: 100%; 5: 0; 11: 12; 12: DN1000-R0; 13: 1.5777; 0: 51
+ 12.6K
Right Curve | bar: 1 to 2
| b | 1: 8.4636; 2: 21.0068
| m | 1: -0.51212; 2: -1.6644
(x,y) | bar: 3 to 4
| Manual dT | 1: 12.6214; 2: 12.6214; 3: 2; 4: 0
[7 empty] | 100% | 10 | -6
|  | dT | dT | mm |  |  |  | 5.6 | 0
[7 empty] | 0% | 2 | 2.4
Guide Ring Settings
[19 empty] | dt | V
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 |  |  | -6 | 10 | slope | -0.25606
| Model | DN250 R1 | DN250 | DN355 R1 | DN355 | DN400 | DN500 R1 | DN500 | DN630 | DN710 R1 | DN710 | DN1000 R1 | DN1000 | DN1340 |  |  | 25.2428 | 2 | int | 8.4636
[17 empty] | 6.93 | 6.6892 | bar: 1 to 13
|  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
|  | -8 | -8 | -8 | -8 | -8 | -8 | -8 | -8 | -8 | -8 | -8 | -8 | -8
| 2x dT | 288.0231 | 201.9424 | 100.3684 | 70.5281 | 49.3023 | 36.0029 | 25.2428 | 12.619 | 12.546 | 8.816 | 4.4843 | 3.1553 | 1.3114
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Max dT | 144.0116 | 100.9712 | 50.1842 | 35.2641 | 24.6512 | 18.0014 | 12.6214 | 6.3095 | 6.273 | 4.408 | 2.2421 | 1.5777 | 0.6557
| Intercept | 2.702% | 3.811% | 7.382% | 10.19% | 13.96% | 18.18% | 24.07% | 38.8% | 38.94% | 47.57% | 64.08% | 71.71% | 85.92%
|  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
| Setting | 5% | 8% | 15% | 20% | 28% | 36% | 48% | 78% | 78% | 95% | 128% | 143% | 172%
| Round <20% | 0% | 0% | 0% | 20% | 28% | 36% | 48% | 78% | 78% | 95% | 128% | 143% | 172%
| Inverse | 1 | 1 | 1 | 0.8 | 0.72 | 0.64 | 0.52 | 0.22 | 0.22 | 0.05 | -0.28 | -0.43 | -72%
| Round | 100% | 100% | 100% | 80% | 70% | 65% | 50% | 20% | 20% | 5% | -30% | -45% | -70%
|  | 13.3 | 13.3 | 18.6 | 18.6 | 20.8 | 26 | 26 | 32.8 | 36.5 | 36.5 | 51 | 51 | 68.3
| Distance | 13.3 | 13.3 | 18.6 | 14.88 | 14.976 | 16.64 | 13.52 | 7.216 | 8.03 | 1.825 | -14.28 | -21.93 | -49.176
| Distance not rounded | 13.3 | 13.3 | 18.6 | 14.88 | 14.56 | 16.9 | 13 | 6.56 | 7.3 | 1.825 | -15.3 | -22.95 | -47.81
Is Min C > Max C
| Max C | - | - | 31.4 | 23.6 |  |  | 19.1 | 18.1 |  |  | 16.3 | 15.9 | 15.3 | 15.1 | 14.8
| Min C | - | - | 10.4 | 8.4 |  |  | 7 | 6.7 |  |  | 6.1 | 6 | 5.8 | 5.7 | 5.6
| Min>Max? | FALSE | FALSE | FALSE | FALSE |  |  | FALSE | FALSE |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Notes & Drawings
SMARTEMP PRODUCT SELECTION CALCULATOR
Adjustable Helical Swirl Diffuser [HSC-AD] Notes
CEILING TYPE
Diffuser can be installed substantially flush with a false ceiling or freely suspended.
ACOUSTICS
Sound power level is valid for diffusers used with round duct connection. For installation with connection boxes, add 6 dB(A). For non-acoustically lined connection boxes, add a further 2 dB(A).
PRE-OCCUPANCY WARM-UP BOOST
For warm-up from a low night setback temperature (cell M27), especially where high infiltration heat loss occurs (e.g. lobbies), consider introducing a Pre-Occupancy Warm-Up Boost mode that increases diffuser airflow by the Airflow Boost Factor (row 61) and pressure by the Pressure Boost Factor (row 62) during pre-occupancy warm-up only. This is typically achieved by either:
1. | Speeding up the supply fan to increase total airflow by the Airflow Boost Factor (row 61); or
2. | By not increasing total airflow, but instead only supplying air to the percentage of Diffusers Active During Warm-Up Boost (row 67), typically achieved by having motorised dampers (by others) shut off airflow to the remaining diffusers (typically to a duct run of diffusers). Round up/down the percentage to avoid fractions of diffusers to which airflow is to be shut-off. Minimise motorised dampers by grouping diffusers to be shut-off onto common ducts. Refer to example below.
Pre-Occupancy Warm-Up is to be deactivated when room temperature setpoint is achieved, and is to remain deactivated until the next warm-up cycle is initiated.
Example of Option 2, above: |  |  | DN500-R1
Selected Airflow |  |  | 500 L/s @ 30.4 Pa static
Room Temperature Setpoint |  |  | 21°C
Night Setback Temperature |  |  | 16°C
Results: | [5 empty] | Explanation:
Row 59 | Thermal Element Setting |  |  |  | 27°C | Supply air to be greater than or equal to 27 °C, otherwise the guide-ring will retract and prevent heat project to the floor.
Row 60 | Warm-Up Max Boost ΔT |  |  |  | +11 K
Row 61 | Warm-Up Airflow Boost Factor |  |  |  | 1.25 | Boosted Airflow per diffuser: 1.25 × 500 L/s = 625 L/s
Row 62 | Warm-Up Pressure Boost Factor |  |  |  | 1.57 | Pressure required to achieve Boosted Airflow: 1.57 × 30.4 = 47.7 Pa
Row 63 | Diffusers Active During Warm-Up Boost |  |  |  | 80% | Boost airflow by supplying the fixed total airflow only to the percentage of Diffusers Active During Warm-Up (80%), achieved by shutting off airflow, via motorised dampers, to the remaining diffusers (i.e. 20%).
DIFFUSER DIMENSIONS
Model | D2 | D4 | E | D5 | L | H1 | H2 | H3 | F | - note: some dimensions currently not available
DN355 | 395 | 530 | 445, 595, 603 | 354 | 495 | 550 | 20 | 80 | 320 | * all dimensions in mm
DN = 355 | D2 = 395 | D4 = 530 | E = 445, 595, 603 | D5 = 354 | L = 495 | H1 = 550 | H2 = 20 | H3 = 80 | F = 320
> 355(1×DN) | 355
D4 = Ø530 OR E = □445, 595, 603
Adjustment Type Description (for 'Product Code Generator')
Symbol | Description
M | Manual adjustment
E1 | Electric actuator 24V, 2-10V
E2 | Electric actuator 24V, 3-pt (2 position)
E3 | Electric actuator 230V, 3-pt (2 position)
T__ | With base module and thermal actuator set to __ (22°C - 30°C, default 26°C).
> 355(1×DN)
H2 = 20
DN = 355
D2 = 395
D4 = Ø530 OR E = □445, 595, 603
D5 = 354
H1 = 550
F = 320
H3 = 80
L = 495

## Heating (hidden)
INPUT TO GREEN CELLS
k | 4.642
| Diameter | [5 empty] | Diameter
DN250 R1 | 0.209 |  |  |  |  | DN250 | 0.25
DN355 R1 | 0.297 |  |  |  |  | DN355 | 0.355
DN500 R1 | 0.418 |  |  |  |  | DN400 | 0.4
DN710 R1 | 0.594 |  |  |  |  | DN500 | 0.5
DN1000 R1 | 0.837 |  |  |  |  | DN630 | 0.63
[6 empty] | DN710 | 0.71
[6 empty] | DN1000 | 1
WITH REDUCER | [5 empty] | NO REDUCER
Diameter | dT | Area | H | Velocity | Flowrate | Diameter | dT | Area | H | Velocity | Flowrate
0.837 | 4 | 0.55023 | 2.5 | 0.80917 | 445.2242 | 1 | 4 | 0.7854 | 2.5 | 0.67579 | 530.7622
|  |  | 3 | 0.971 | 534.2691 |  |  |  | 3 | 0.81094 | 636.9146
|  |  | 4 | 1.2947 | 712.3588 |  |  |  | 4 | 1.0813 | 849.2195
|  |  | 5 | 1.6183 | 890.4485 |  |  |  | 5 | 1.3516 | 1061.5244
|  |  | 6 | 1.942 | 1068.5382 |  |  |  | 6 | 1.6219 | 1273.8293
|  |  | 7 | 2.2657 | 1246.6279 |  |  |  | 7 | 1.8922 | 1486.1342
|  |  | 8 | 2.5893 | 1424.7176 |  |  |  | 8 | 2.1625 | 1698.4391
|  |  | 9 | 2.913 | 1602.8073 |  |  |  | 9 | 2.4328 | 1910.7439
|  |  | 10 | 3.2367 | 1780.897 |  |  |  | 10 | 2.7031 | 2123.0488
|  |  | 11 | 3.5603 | 1958.9867 |  |  |  | 11 | 2.9735 | 2335.3537
|  |  | 12 | 3.884 | 2137.0763 |  |  |  | 12 | 3.2438 | 2547.6586
|  |  | 13 | 4.2077 | 2315.166 |  |  |  | 13 | 3.5141 | 2759.9635
|  |  | 14 | 4.5313 | 2493.2557 |  |  |  | 14 | 3.7844 | 2972.2684
|  |  | 15 | 4.855 | 2671.3454 |  |  |  | 15 | 4.0547 | 3184.5732
[9 empty] | 16 | 4.325 | 3396.8781

## HSC-AD data (hidden)
| 95% | 0.2
| 90% | 0.25
| 80% | 0.29
| 70% | 0.33
Product code
|  |  | DN | R
|  | 1 | 250 | 1
|  | 2 | 250 | 0
|  | 3 | 355 | 1
|  | 4 | 355 | 0
|  | 5 | 400 | 0
|  | 6 | 500 | 1
|  | 7 | 500 | 0
|  | 8 | 630 | 0
|  | 9 | 710 | 1
|  | 10 | 710 | 0
|  | 11 | 1000 | 1
|  | 12 | 1000 | 0
|  | 13 |  |  |  |  | - option not available for size DN710 and DN1000
|  | 14 |  |  |  |  | - option not available for DN250 - DN500
| Model | 0 | #N/A | #N/A |  | warning
| Mode Code | #N/A
Adjustment
| Thermal El. Result | T-setting Number |  |  | ‡ moderately elevated air velocities in heating
| Thermal El. Note | T-Setting Note |  |  | † slightly elevated air velocities in heating
0
|  | 1 | M | M | Manual adjustment | Manual
|  | 2 | 24V Elec. motor 2-10V | E1 | Electric actuator 24V; 2-10V | Electric
|  | 3 | 24V Elec. motor 2-position | E2 | Electric actuator 24V; 3-pt (2 position) | Electric
|  | 4 | 230V Elec. motor 2-position | E3 | Electric actuator 230V; 3-pt (2 position) | Electric
|  | 5 | #N/A | #N/A | #N/A | Thermal element |  | grey shade | FALSE
|  | 1 | M | #N/A | Manual adjustment
Selection Table
|  | 1 | 2 | 3 | 4 | 5 |  |  | Closed Ceiling | Open Ceiling
| Face Size | 250 | C375 | S295 | <face> | 375 |  |  | S295 | C375
|  | 355 | C530 | S595 | <face> | 530 |  |  | S595 | C530
|  | 400 | C600 | S595 | <face> | 600 |  |  | S595 | C600
|  | 500 | C750 | <face> | <face> | 750 |  |  | S595 | C750
|  | 630 | C900 | <face> | <face> | 900 |  |  | C900 | C900
|  | 710 | C1000 | <face> | <face> | 1000 |  |  | C1000 | C1000
|  | 1000 | C1420 | <face> | <face> | 1420 |  |  | C1420 | C1420
|  |  | 1 | 2 | 3 | 4 | 5
|  | Table | #N/A | #N/A | #N/A
|  |  | #N/A | #N/A |  |  |  | □ | ø
SELECTION
|  | 1 | #N/A
|  | size | #N/A
|  | Shape | #N/A | #N/A
|  | Description | #N/A
|  | Selection Code | #N/A
| Colour | 1 | RAL9003 | RAL9003 (signal white)
|  | 2 | RAL9005 | RAL9005 (jet black)
|  | 3 | RAL9006 | RAL9006 (white aluminium)
|  | 4 | <colour> | custom colour
|  | 1 | RAL9003
| Accessories | 1 | 0 | Diffuser only
|  | 2 | K | With uninsulated connection box
|  | 3 | B | With mounting bracket (for round duct connection)
|  | 1 | 0 | Diffuser only
| Code |  | select size to generate order code
| Size |  | D2 | D4 | E | D5 | L | H1 | H2 | H3 | F
| 1 | DN250 | 270 | 375 | 295 | 249 | 425 | 400 | 14 | 60 | 215 | 250
| 2 | DN355 | 395 | 530 | 445, 595, 603 | 354 | 495 | 550 | 20 | 80 | 320 | 355
| 3 | DN400 | 447 | 600 | 595, 603 | 399 | 555 | 550 | 19 | 84 | 365 | 400
| 4 | DN500 | 560 | 750 | 595, 603 | 499 | 695 | 690 | 28 | 100 | 465 | 500
| 5 | DN630 | 703 | 900 |  |  |  |  | 33 | 217 | 390 | 630
| 6 | DN710 | 790 | 1000 |  |  |  |  | 32.2 | 240 | 440 | 710
| 7 | DN1000 | 1110 | 1420 |  |  |  |  | 44 | 295 | 640 | 1000
description
| Size | #N/A | #N/A
#N/A
Manual adjustment
| Colour | Powder coated to RAL9003 (signal white)
| Acc | Diffuser only
summary
|  | please select valid size from 'HSC-AD' worksheet | Format
2 |  | 0
3 | Max Airflow [L/s] | Max Airflow [L/s] | #VALUE!
4 | Airflow @ Max Pressure [L/s] | Airflow @ Max Pressure [L/s] | #VALUE!
5 | Min Airflow (Turndown To) [L/s] | Min Airflow (Turndown To) [L/s] | #VALUE!
6 | Min Permissible Airflow [L/s] | Min Permissible Airflow [L/s] | #VALUE!
7 | Static Pressure | Static Pressure | #VALUE!
8 | Total Pressure | Total Pressure
9 | Max Permissible P | Max Permissible P
10 | Sound Power Level | Sound Power Level | #VALUE!
11 | ΔT_max (heating) | ΔT_max (heating) | #VALUE!
12 | T n.s. | T n.s.
13 | Cmax - Centre | Cmax - Centre
14 | Cmax - Perimeter | Cmax - Perimeter | #VALUE!
15 | Cmin | Cmin | #VALUE!
16 | Hmin | Hmin | #VALUE!
17 | Mean Air Velocity | Mean Air Velocity | #VALUE!
18 | Draft Rating | Draft Rating | #VALUE!
19 | PPD | PPD | #VALUE!
20 | PPD Class | PPD Class
21 | PMV | PMV | PMV
22 | T s. | T s. | T s.
23 | Warm-up DT | Warm-up DT
24 | Warm-Up Airflow Boost | Warm-Up Airflow Boost
25 | Warm-Up Pressure Boost | Warm-Up Pressure Boost
26 | Diffuser shut off % | Diffuser shut off %
27 | ΔT_max (heating) | ΔT_max (heating)
28 | Recommended Spigot Dia. | Recommended Spigot Dia.
29 | T-setting Number | T-setting Number
30 | T-Setting Note | T-Setting Note
31 | T-setting Category | T-setting Category | #N/A
max heating | #N/A | #N/A |  | high | moderately elevated air velocities in heating
guide ring | #N/A | selected heating ΔT |  | mid | slightly elevated air velocities in heating
turndown % | 100
dT | -12
Selected C | 11.4532
Spec. airflow | 6.1 | L/s/m²
input diffuser height | 6
room temp | 23
selected heating dt | 4
Selected Airflow | #VALUE!
Min Airflow | #VALUE!
Min Permissible Airflow | #VALUE!
Max Heating | #N/A | #N/A
Thermal element setting | TT s.
Guide Ring | selected heating ΔT
Ceiling location | 2 | 1 = ceiling; 2 = free
Adjustment
Manual mode | Manual Adjustment selected
selected heating ΔT
not recommended
Selection | Manual adjustment
| Sound Power level | #VALUE!
Diagram
#VALUE!
Selected Diffuser Height = 6 m
| Cmin | Cmax
| #VALUE! | #VALUE!
#VALUE!
#VALUE!
Average
C select | 11.5
Average C = 11.5 m
Top box | #VALUE! | 1 | Specific Airflow Rate = 6.1 L/s/m² @ Average C = 11.5 m
box 2 | #VALUE! | 2 | Specific Airflow Rate = 6.1 L/s/m² @ Selected C = 11.5 m
box 3 | Average C = 11.5 m | 3 | Selected Specific Airflow Rate: 6.1 L/s/m²
room box | Specific Airflow Rate = 6.1 L/s/m² @ Average C = 11.5 m
bottom box | Recommended distances for ≥ 90% ADPI (selected)
Comfort Performance
ADPI | ≥ 90%
Insatll | Freely Suspended
Mean Room Air Velocity | #VALUE!
Mean Draught Rating @ 23 °C | #VALUE!
Mean PPD | #VALUE!
Satisfies PPD (ISO7730) | Category PPD Class
Mean PMV ^ | -PMV ≤ PMV ≤ PMV
Adjustment | M
Temperature note
Notes Front Page
Comfort note | Comfort criteria valid for average diffuser spacing of 11.5 m & room temperature of 23 °C (see cells K14 & L23)
guide ring dist selected |  | Note ¹ : 'Guide Ring Position' is measured from diffuser face to guide ring trailing edge.
guide ring dist warnign |  | Note ¹ Warning: Selected ΔT (heating) > recommended max ΔT
Cminmax warning |  | Warning: Threat of draught when Cmin > Cmax. Consider increasing turndown % (Cell E11)
thermal element warning | 'n.r.' - thermal element not recommended; consider electric actuator ‡ moderately elevated air velocities in heating † slightly elevated air velocities in heating | 'n.r.' - thermal element not recommended; consider electric actuator | ‡ moderately elevated air velocities in heating † slightly elevated air velocities in heating

## Charts (hidden)
Chart
Title | DN500-R0 Recommended Actuator Control (V) & Guide Ring Position (mm) for 6 m discharge
DN500-R0 Recommended Actuator Control (V) & Guide Ring Position (mm) for 6 m discharge
7 mm
26 mm
20 mm
13 mm
0 mm
cooling
heating

## Selection Summary & Print
| HSC-AD Performance Calculator Summary |  |  |  | HSC-AD Performance Calculator Summary
Project | <Name> |  |  | Direction Adjustment | Manual adjustment
Company | <Name>
Consultant | <Name>
|  |  |  | Description | #N/A
Product | SMARTEMP HSC-AD |  |  |  | #N/A
| Adjustable Helical Swirl Diffuser |  |  |  | Manual adjustment
Size | please select valid size from 'HSC-AD' worksheet |  |  |  | Powder coated to RAL9003 (signal white)
Guide Ring Adjustment Type | Manual adjustment |  |  |  | Diffuser only
Project Summary |  |  |  | Order Code (select to copy) | select size to generate order code
Selected Airflow Rate | #VALUE!
Min Selected Airflow | #VALUE! |  |  | Control Curve | Control voltage only for Electric Motor Adjustment Type 24V 2-10V (E1)
Min Permissible Airflow | #VALUE! |  |  |  | Guide ring position is the recessed distance as measured from the diffuser face to the bottom of the guide ring. Use curve as a guide for Manual Adjustment
Max Recommended Heating ΔT | #N/A
Acoustic Performance
Sound Power Level | #VALUE!
Comfort Performance & Recommended Layout
ADPI | ≥ 90% | ADPI valid for cooling in horizontal mode only
Selected Installation | Freely Suspended
Mean Room Air Velocity | #VALUE!
Mean Draught Rating | #VALUE!
Mean PPD | #VALUE!
Satisfies PPD (ISO7730) | Category PPD Class
Mean PMV * | -PMV ≤ PMV ≤ PMV
* ISO7730; ASHRAE Std 55
|  |  | v 7.15 [01/25] |  |  | v 7.15 [01/25]
#VALUE!
#VALUE!
Average C = 11.5 m
#VALUE!
Specific Airflow Rate = 6.1 L/s/m² @ Average C = 11.5 m
C2
Selected Diffuser Height = 6 m
Recommended distances for ≥ 90% ADPI (selected)

## Tender Text (hidden)
Furnish and install SMARTEMP® Adjustable Helical Swirl Diffusers, type HSC-AD, to provide diffuse airflow with adjustable horizontal-to-vertical discharge direction for high thermal comfort from elevated discharge heights. Each diffuser is to be made of powder coated steel and shall include 20 off-set radial vanes flush with the horizontal diffuser face. The diffuser face is to be square (up to neck size DN500 only) or circular, as specified. The diffuser is to be installed substantially flush
with the suspended false ceiling or freely suspended, as specified.
Swirl vanes are to include cambered leading edges for reduced noise and pressure drop, and the helical swirl vane tips are each to incorporate a geometric twist for increased downward discharge penetration and reduced minimum airflow rates. An internal adjustable guide ring with 20 geometrically twisted guide vanes is to provide constant pressure discharge direction adjustment.
The guide ring is to be adjusted manually, electrically or thermally, as specified and in accordance with SMARTEMP guidelines. The latter two each attach as a kit to an included control module, which is optionally available for manual adjustment. Diffuser neck size is to be DN250, DN355, DN500 or DN710, as required. The diffuser is to incorporate the optional reducer and reduced guide ring, where appropriate. Diffuser discharge height of 2.5 to 15 m to be inaccordance with SMARTEMP's recommendations for the duty required.
Cooling with horizontal discharge direction to be at no less than ΔTsupply-room = -13 K. For heating applications, provide downward discharge and control maximum ΔTsupply-room no t to exceed the maximum per missible heating temperature differential prescribed by SMARTEMP for the selected diffuser, airflow rate and discharge height.
Where specified, each diffuser is to be connected to a side-entry sheet-metal connections box, internally insulated where indicated, fabricated in accordance with SMARTEMP's recommendations. Alternatively, each diffuser is to be connected to a vertical duct of internal diameter equal to the diffuser DN size and at least one duct diameter in length.