## Tables Old (hidden)
[5 empty] | K= | 0.015
Flange Dimensions |  |  | Face |  | K1= | 2 | [36 empty] | Input Airflow Rate
Width | 613 | [mm] | 573 |  | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240 | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 | 360 | 370 | 380 | 390 | [L/s] | 70 | L/s
|  |  | Min Discharge Height |  | K1= 30: 2.1; 2 100: 2.1; 2 150: 2.1; 2 250: 2.5
| 134 | 1-row | 94 | Pt | K1= 30: 3.5625; 2 40: 6.3886; 2 50: 10.0497; 2 60: 14.5515; 2 70: 19.8987; 2 80: 26.0951; 2 90: 33.1443; 2 100: 41.0493; 2 110: 49.8128 | [Pa] | 19.8987 | Pa
|  | 0.054 |  | Lp* | K1= 30: < 5; 2 40: < 5; 2 50: 9.3132; 2 60: 15.1493; 2 70: 20.0837; 2 80: 24.358; 2 90: 28.1283; 2 100: 31.5009; 2 110: 34.5517; 2 290: Key | [NC] | 20.0837 | NC
[5 empty] | 1.653 | 2.204 | 2.755 | 3.306 | 3.857 | 4.408 | 4.959 | 5.51 | 6.061
[5 empty] | 3.306 | 4.408 | 5.51 | 6.612 | 7.714 | 8.816 | 9.918 | 11.02 | 12.122
| 173 | 2-row | 133 | Pt | 2 50: 4.9677; 2 60: 7.193; 2 70: 9.8361; 2 80: 12.8991; 2 90: 16.3836; 2 100: 20.2911; 2 110: 24.623; 2 120: 29.3806; 2 130: 34.5648; 2 140: 40.1768; 2 150: 46.2175; 2 290: ≤ 20; 2 300: ≤ 30; 2 310: ≤ 40; 2 320: ≤ 50; 2 330: Pa | [Pa] | 9.8361 | Pa
Height |  | 0.076 |  | Lp* | 2 50: < 5; 2 60: 5.5474; 2 70: 10.4817; 2 80: 14.7561; 2 90: 18.5263; 2 100: 21.8989; 2 110: 24.9498; 2 120: 27.735; 2 130: 30.2972; 2 140: 32.6694; 2 150: 34.8778; 2 290: ≤ 25; 2 300: ≤ 30; 2 310: ≤ 35; 2 320: ≤ 40; 2 330: NC | [NC] | 10.4817 | NC
[7 empty] | 2.3223 | 2.7867 | 3.2512 | 3.7156 | 4.1801 | 4.6445 | 5.109 | 5.5734 | 6.0379 | 6.5023 | 6.9668 | [13 empty] | 3 | 3.5 | 4 | 4.5 | m
[7 empty] | 4.6445 | 5.5734 | 6.5023 | 7.4312 | 8.3601 | 9.289 | 10.2179 | 11.1468 | 12.0757 | 13.0046 | 13.9335 | [13 empty] | 6 | 7 | 8 | 9 | m
[mm] | 212 | 3-row | 172 | Pt | 2 60: 4.2676; 2 70: 5.8358; 2 80: 7.653; 2 90: 9.7204; 2 100: 12.0387; 2 110: 14.6088; 2 120: 17.4315; 2 130: 20.5073; 2 140: 23.8369; 2 150: 27.4208; 2 160: 31.2597; 2 170: 35.3539; 2 180: 39.704; 2 190: 44.3104; 2 200: 49.1735; 2 290: * Based on 10 dB room absorption | [Pa] | 5.8358 | Pa
|  | 0.098 |  | Lp* | 2 60: < 5; 2 70: 3.3673; 2 80: 7.6416; 2 90: 11.4118; 2 100: 14.7844; 2 110: 17.8353; 2 120: 20.6205; 2 130: 23.1827; 2 140: 25.5549; 2 150: 27.7634; 2 160: 29.8292; 2 170: 31.7698; 2 180: 33.5995; 2 190: 35.3302; 2 200: 36.9721 | [NC] | 3.3673 | NC
[8 empty] | 2.4541 | 2.8631 | 3.2721 | 3.6811 | 4.0901 | 4.4991 | 4.9081 | 5.3171 | 5.7261 | 6.1351 | 6.5442 | 6.9532 | 7.3622 | 7.7712 | 8.1802
[8 empty] | 4.9081 | 5.7261 | 6.5442 | 7.3622 | 8.1802 | 8.9982 | 9.8162 | 10.6343 | 11.4523 | 12.2703 | 13.0883 | 13.9063 | 14.7244 | 15.5424 | 16.3604
| 251 | 4-row | 211 | Pt | 2 70: 3.854; 2 80: 5.0541; 2 90: 6.4194; 2 100: 7.9504; 2 110: 9.6478; 2 120: 11.5119; 2 130: 13.5431; 2 140: 15.742; 2 150: 18.1089; 2 160: 20.6441; 2 170: 23.348; 2 180: 26.2208; 2 190: 29.2629; 2 200: 32.4745; 2 210: 35.8559; 2 220: 39.4074; 2 230: 43.1292; 2 240: 47.0215 | [Pa] | 3.854 | Pa
|  | 0.121 |  | Lp* | 2 70: < 5; 2 80: 1.9875; 2 90: 5.7577; 2 100: 9.1303; 2 110: 12.1812; 2 120: 14.9664; 2 130: 17.5286; 2 140: 19.9008; 2 150: 22.1092; 2 160: 24.1751; 2 170: 26.1157; 2 180: 27.9453; 2 190: 29.676; 2 200: 31.3179; 2 210: 32.8797; 2 220: 34.3688; 2 230: 35.7917; 2 240: 37.154 | [NC] | -2.2869 | NC
[9 empty] | 2.5766 | 2.9447 | 3.3128 | 3.6809 | 4.049 | 4.4171 | 4.7852 | 5.1533 | 5.5214 | 5.8894 | 6.2575 | 6.6256 | 6.9937 | 7.3618 | 7.7299 | 8.098 | 8.4661 | 8.8342
[9 empty] | 5.1533 | 5.8894 | 6.6256 | 7.3618 | 8.098 | 8.8342 | 9.5703 | 10.3065 | 11.0427 | 11.7789 | 12.5151 | 13.2512 | 13.9874 | 14.7236 | 15.4598 | 16.196 | 16.9321 | 17.6683
FACE (active size mm)
Width | 747.5 | [mm] | 707.5 |  |  | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240 | 250 | 260 | 270 | 280 | 290 | 300 | [9 empty] | [L/s]
| 134 | 1-row | 94 | Pt |  | 40: 4.1639; 50: 6.5501; 60: 9.4842; 70: 12.9692; 80: 17.0079; 90: 21.6023; 100: 26.7545; 110: 32.4662; 120: 38.7392; 130: 45.5748 | [9 empty] | [Pa] | 12.9692 | Pa
|  | 0.066505 |  | Lp* |  | 40: < 5; 50: 4.5727; 60: 10.4088; 70: 15.3432; 80: 19.6175; 90: 23.3878; 100: 26.7603; 110: 29.8112; 120: 32.5965; 130: 35.1586 | [9 empty] | [NC] | 15.3432 | NC
[6 empty] | 1.888 | 2.36 | 2.832 | 3.304 | 3.7761 | 4.2481 | 4.7201 | 5.1921 | 5.6641 | 6.1361
[6 empty] | 3.7761 | 4.7201 | 5.6641 | 6.6081 | 7.5521 | 8.4961 | 9.4401 | 10.3842 | 11.3282 | 12.2722
| 173 | 2-row | 133 | Pt |  | 50: 3.2378; 60: 4.6881; 70: 6.4108; 80: 8.4072; 90: 10.6783; 100: 13.225; 110: 16.0484; 120: 19.1492; 130: 22.5281; 140: 26.1858; 150: 30.123; 160: 34.3401; 170: 38.8378; 180: 43.6166; 190: 48.6769 | [9 empty] | [Pa] | 6.4108 | Pa
Height |  | 0.094098 |  | Lp* |  | 50: < 5; 60: < 5; 70: 5.7412; 80: 10.0156; 90: 13.7858; 100: 17.1584; 110: 20.2093; 120: 22.9945; 130: 25.5567; 140: 27.9289; 150: 30.1373; 160: 32.2032; 170: 34.1438; 180: 35.9734; 190: 37.7041 | [9 empty] | [NC] | 5.7412 | NC
[7 empty] | 1.9841 | 2.3809 | 2.7777 | 3.1745 | 3.5713 | 3.9681 | 4.365 | 4.7618 | 5.1586 | 5.5554 | 5.9522 | 6.349 | 6.7458 | 7.1426 | 7.5395
[7 empty] | 3.9681 | 4.7618 | 5.5554 | 6.349 | 7.1426 | 7.9363 | 8.7299 | 9.5235 | 10.3172 | 11.1108 | 11.9044 | 12.698 | 13.4917 | 14.2853 | 15.0789
[mm] | 212 | 3-row | 172 | Pt |  |  |  | 2.7815 | 3.8035 | 4.988 | 6.3354 | 7.8464 | 9.5215 | 11.3612 | 13.3659 | 15.536 | 17.8719 | 20.3739 | 23.0424 | 25.8777 | 28.8799 | 32.0496 | 35.3867 | 38.8917 | 42.5648 | 46.4062 | 50.416 | [14 empty] | [Pa] | 3.8035 | Pa
|  | 0.12169 |  | Lp* |  |  |  | < 5 | < 5 | < 5 | 6.6713 | 10.0439 | 13.0948 | 15.88 | 18.4422 | 20.8144 | 23.0229 | 25.0887 | 27.0293 | 28.859 | 30.5897 | 32.2316 | 33.7933 | 35.2824 | 36.7053 | 38.0677 | 39.3744 | [14 empty] | [NC] | -1.3732 | NC
[8 empty] | 2.0936 | 2.4426 | 2.7915 | 3.1404 | 3.4894 | 3.8383 | 4.1873 | 4.5362 | 4.8851 | 5.2341 | 5.583 | 5.9319 | 6.2809 | 6.6298 | 6.9788 | 7.3277 | 7.6766 | 8.0256 | 8.3745 | 8.7234
[8 empty] | 4.1873 | 4.8851 | 5.583 | 6.2809 | 6.9788 | 7.6766 | 8.3745 | 9.0724 | 9.7703 | 10.4681 | 11.166 | 11.8639 | 12.5618 | 13.2596 | 13.9575 | 14.6554 | 15.3533 | 16.0511 | 16.749 | 17.4469
| 251 | 4-row | 211 | Pt |  |  |  |  | 2.5119 | 3.2941 | 4.1839 | 5.1818 | 6.2881 | 7.503 | 8.8269 | 10.2601 | 11.8027 | 13.4551 | 15.2174 | 17.0898 | 19.0725 | 21.1657 | 23.3696 | 25.6844 | 28.1101 | 30.647 | 33.2951 | 36.0547 | 38.9258 | 41.9086 | 45.0031 | 48.2097 | [9 empty] | [Pa] | 2.5119 | Pa
|  | 0.14928 |  | Lp* |  |  |  |  | < 5 | < 5 | < 5 | < 5 | 7.4407 | 10.2259 | 12.7881 | 15.1603 | 17.3687 | 19.4346 | 21.3752 | 23.2048 | 24.9355 | 26.5774 | 28.1392 | 29.6283 | 31.0512 | 32.4135 | 33.7202 | 34.9757 | 36.1838 | 37.3479 | 38.4712 | 39.5564 | [9 empty] | [NC] | -7.0274 | NC
[9 empty] | 2.2053 | 2.5204 | 2.8354 | 3.1504 | 3.4655 | 3.7805 | 4.0956 | 4.4106 | 4.7257 | 5.0407 | 5.3557 | 5.6708 | 5.9858 | 6.3009 | 6.6159 | 6.931 | 7.246 | 7.5611 | 7.8761 | 8.1911 | 8.5062 | 8.8212 | 9.1363 | 9.4513
[9 empty] | 4.4106 | 5.0407 | 5.6708 | 6.3009 | 6.931 | 7.5611 | 8.1911 | 8.8212 | 9.4513 | 10.0814 | 10.7115 | 11.3416 | 11.9717 | 12.6018 | 13.2318 | 13.8619 | 14.492 | 15.1221 | 15.7522 | 16.3823 | 17.0124 | 17.6425 | 18.2726 | 18.9026
FACE (active size mm)
Width | 950 | [mm] | 910 |  |  |  | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240 | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 | 360 | 370 | 380 | 390 | [L/s]
| 134 | 1-row | 94 | Pt |  |  | 50: 3.9293; 60: 5.6894; 70: 7.7801; 80: 10.2028; 90: 12.9589; 100: 16.0496; 110: 19.476; 120: 23.2391; 130: 27.3397; 140: 31.7786; 150: 36.5566; 160: 41.6744; 170: 47.1327 | [Pa] | 7.7801 | Pa
|  | 0.08554 |  | Lp* |  |  | 50: < 5; 60: < 5; 70: 7.286; 80: 11.5604; 90: 15.3306; 100: 18.7032; 110: 21.7541; 120: 24.5393; 130: 27.1015; 140: 29.4737; 150: 31.6821; 160: 33.748; 170: 35.6886 | [NC] | 7.286 | NC
[7 empty] | 1.9184 | 2.302 | 2.6857 | 3.0694 | 3.4531 | 3.8367 | 4.2204 | 4.6041 | 4.9878 | 5.3714 | 5.7551 | 6.1388 | 6.5225
[7 empty] | 3.8367 | 4.6041 | 5.3714 | 6.1388 | 6.9061 | 7.6735 | 8.4408 | 9.2082 | 9.9755 | 10.7429 | 11.5102 | 12.2776 | 13.0449
| 173 | 2-row | 133 | Pt |  |  | 70: 3.8458; 80: 5.0434; 90: 6.4057; 100: 7.9335; 110: 9.6272; 120: 11.4873; 130: 13.5143; 140: 15.7085; 150: 18.0703; 160: 20.6001; 170: 23.2982; 180: 26.165; 190: 29.2006; 200: 32.4054; 210: 35.7796; 220: 39.3235; 230: 43.0374; 240: 46.9214 | [Pa] | 3.8458 | Pa
Height |  | 0.12103 |  | Lp* |  |  | 70: < 5; 80: < 5; 90: 5.7286; 100: 9.1012; 110: 12.1521; 120: 14.9374; 130: 17.4995; 140: 19.8717; 150: 22.0802; 160: 24.1461; 170: 26.0866; 180: 27.9163; 190: 29.647; 200: 31.2889; 210: 32.8507; 220: 34.3398; 230: 35.7627; 240: 37.125 | [NC] | -2.3159 | NC
[9 empty] | 2.2579 | 2.5804 | 2.903 | 3.2255 | 3.5481 | 3.8706 | 4.1932 | 4.5157 | 4.8383 | 5.1608 | 5.4834 | 5.8059 | 6.1285 | 6.451 | 6.7736 | 7.0961 | 7.4187 | 7.7413
[9 empty] | 4.5157 | 5.1608 | 5.8059 | 6.451 | 7.0961 | 7.7413 | 8.3864 | 9.0315 | 9.6766 | 10.3217 | 10.9668 | 11.6119 | 12.257 | 12.9021 | 13.5472 | 14.1923 | 14.8374 | 15.4825
[mm] | 212 | 3-row | 172 | Pt | [6 empty] | 3.8005 | 4.707 | 5.7118 | 6.8154 | 8.018 | 9.3198 | 10.7211 | 12.222 | 13.8228 | 15.5237 | 17.3247 | 19.2261 | 21.228 | 23.3306 | 25.534 | 27.8384 | 30.2439 | 32.7505 | 35.3585 | 38.068 | 40.879 | 43.7916 | 46.8061 | 49.9224 | [7 empty] | [Pa] | 2.2817 | Pa
|  | 0.15652 |  | Lp* | [6 empty] | < 5 | < 5 | 5.0377 | 7.8229 | 10.3851 | 12.7573 | 14.9657 | 17.0316 | 18.9722 | 20.8018 | 22.5325 | 24.1744 | 25.7362 | 27.2253 | 28.6482 | 30.0105 | 31.3172 | 32.5727 | 33.7808 | 34.9449 | 36.0682 | 37.1534 | 38.203 | 39.2192 | [7 empty] | [NC] | -9.4304 | NC
[11 empty] | 2.5527 | 2.8364 | 3.12 | 3.4036 | 3.6873 | 3.9709 | 4.2545 | 4.5382 | 4.8218 | 5.1055 | 5.3891 | 5.6727 | 5.9564 | 6.24 | 6.5236 | 6.8073 | 7.0909 | 7.3745 | 7.6582 | 7.9418 | 8.2255 | 8.5091 | 8.7927 | 9.0764
[11 empty] | 5.1055 | 5.6727 | 6.24 | 6.8073 | 7.3745 | 7.9418 | 8.5091 | 9.0764 | 9.6436 | 10.2109 | 10.7782 | 11.3454 | 11.9127 | 12.48 | 13.0473 | 13.6145 | 14.1818 | 14.7491 | 15.3164 | 15.8836 | 16.4509 | 17.0182 | 17.5854 | 18.1527
| 251 | 4-row | 211 | Pt | [8 empty] | 3.7721 | 4.501 | 5.2952 | 6.1549 | 7.0803 | 8.0715 | 9.1287 | 10.2519 | 11.4413 | 12.697 | 14.0191 | 15.4077 | 16.8629 | 18.3847 | 19.9733 | 21.6287 | 23.351 | 25.1404 | 26.9968 | 28.9203 | 30.911 | 32.9691 | 35.0944 | 37.2872 | 39.5474 | 41.8752 | 44.2705 | 46.7335 | 49.2641 | [Pa] | 1.5068 | Pa
|  | 0.19201 |  | Lp* | [8 empty] | < 5 | < 5 | 4.7309 | 7.1031 | 9.3116 | 11.3775 | 13.3181 | 15.1477 | 16.8784 | 18.5203 | 20.0821 | 21.5712 | 22.9941 | 24.3564 | 25.6631 | 26.9186 | 28.1266 | 29.2908 | 30.414 | 31.4992 | 32.5488 | 33.5651 | 34.5501 | 35.5057 | 36.4336 | 37.3353 | 38.2124 | 39.066 | 39.8975 | [NC] | -15.0845 | NC
[13 empty] | 2.8169 | 3.073 | 3.3291 | 3.5852 | 3.8413 | 4.0974 | 4.3535 | 4.6095 | 4.8656 | 5.1217 | 5.3778 | 5.6339 | 5.89 | 6.146 | 6.4021 | 6.6582 | 6.9143 | 7.1704 | 7.4265 | 7.6826 | 7.9386 | 8.1947 | 8.4508 | 8.7069 | 8.963 | 9.2191 | 9.4752 | 9.7312 | 9.9873
[13 empty] | 5.6339 | 6.146 | 6.6582 | 7.1704 | 7.6826 | 8.1947 | 8.7069 | 9.2191 | 9.7312 | 10.2434 | 10.7556 | 11.2678 | 11.7799 | 12.2921 | 12.8043 | 13.3164 | 13.8286 | 14.3408 | 14.8529 | 15.3651 | 15.8773 | 16.3895 | 16.9016 | 17.4138 | 17.926 | 18.4381 | 18.9503 | 19.4625 | 19.9747

## PMW-AD DN600,950,1500
SMARTEMP PRODUCT SELECTION CALCULATOR
Perforated Multistream Diffuser [PMW-AD]
Project: | <Project Name>
Inputs | [7 empty] | Optional | [11 empty] | v 3.8 [11/2023]
| Maximum Airflow Rate | 120 | L/s | m3/h | [5 empty] | ADPI ≥ | 90% |  |  | default ≥ 90%
| VAV: Turndown to | 100 | % | 50% to 100% |  |  |  | Draught Rating & Heating
use 100% for CAV
| Maximum Total Pressure | 30 | Pa | default 30 Pa |  |  |  |  | Auto Selection: Average Throw Length and Breadth = 3.9 L/s/m²
| Diffuser Height | 2.5 | m | 2.0 m to 5.5 m (recommended) | [5 empty] | Manual Throw: Length | 5.2 |  | m
[10 empty] | Manual Throw: Breadth | 3.5 |  | m | = specific airflow: 6.6 L/s/m²
| ΔT (cooling) | -12 | K | 0 K to -15 K
|  |  |  | (use -8 K for 0 to -8 K) | [5 empty] | Specific Airflow Rate | 9.8 |  | L/s/m² | = floor area: 12.2 m²
[10 empty] | Room Temperature | 23 |  | °C | 20 °C to 26 °C (default 23 °C)
Thermal Comfort Guide
[9 empty] | ADPI ≥ 95%; ṽ ≤ 0.20 m/s: | Premium comfort, sedentary activity, such as in auditoria.
[9 empty] | ADPI ≥ 90%; ṽ ≤ 0.25 m/s: | High comfort near-sedentary activity, such as in board rooms, high end offices and libraries.
[9 empty] | ADPI ≥ 80%; ṽ ≤ 0.29 m/s: | Good comfort near sedentary activity, such as open-plan offices and meeting rooms.
[9 empty] | ADPI ≥ 70%; ṽ ≤ 0.33 m/s: | Standard comfort medium activity, such as in transient spaces, retail and lobbies.
PMW-AD- |  |  |  | DN600 |  |  |  | DN950 |  |  |  | DN1500 |  |  |  | Key: | Suitable | Not Suitable | Warning
Rows (Height) |  | Hr |  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | * | Based on 10dB room absorption
Neck | Width | Wn | [mm] | DN600 1: 577; DN950 1: 915; DN1500 1: 1455 | Throw Setting Guide
| Height | Hn | [mm] | 99 | 138 | 177 | 216 | 99 | 138 | 177 | 216 | 99 | 138 | 177 | 216
Face | Width | Wf | [mm] | DN600 1: 612; DN950 1: 950; DN1500 1: 1490
| Height | Hf | [mm] | 134 | 173 | 212 | 251 | 134 | 173 | 212 | 251 | 134 | 173 | 212 | 251
Total Pressure |  | Pt | [Pa] | 52.8 | 26.9 | 16.2 | 10.8 | 20.7 | 10.5 | 6.4 | 4.2 | 8.1 | 4.1 | < 3 | < 3
Min Recommended Flow Rate |  | Vmin | [L/s] | 28.7 | 40.1 | 51.4 | 62.7 | 45.6 | 63.5 | 81.5 | 99.4 | 72.5 | 101 | 129.6 | 158.1
Sound Power Level |  | Lw | [dB(A)] | 50.7 | 41.5 | 34.6 | 29.1 | 38 | 28.8 | 21.9 | 16.4 | 25.1 | 15.9 | < 15 | < 15
Sound Pressure Level * |  | Lp | [NC] | 35.7 | 26.5 | 19.6 | 14.1 | 23 | 13.8 | 6.9 | < 5 | 10.1 | < 5 | < 5 | < 5
Min Recommended Diffuser Height |  | Hmin | [m] | 2.4 | 2.4 | 2.4 | 2.4 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2
Throw Setting | Short (S) | Lmin | [m] | 2.6 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.4 | 2.4 | 2.5 | 2.4 | 2.4 | 2.4
|  | Lmax | [m] | 7.6 | 6.7 | 5.9 | 5.4 | 6.2 | 5.4 | 4.8 | 4.3 | 5.1 | 4.3 | 3.8 | 3.4
|  | Bmin | [m] | 4.5 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.2 | 4.2 | 4.3 | 4.2 | 4.2 | 4.2
|  | Bmax | [m] | 13.2 | 11.5 | 10.3 | 9.4 | 10.8 | 9.4 | 8.3 | 7.5 | 8.8 | 7.4 | 6.6 | 5.9
| Medium (M) (default) | Lmin | [m] | 3.4 | 3.3 | 3.3 | 3.2 | 3.3 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
|  | Lmax | [m] | 10 | 8.8 | 7.8 | 7.2 | 8.2 | 7.1 | 6.3 | 5.7 | 6.7 | 5.6 | 5 | 4.5
|  | Bmin | [m] | 3.4 | 3.3 | 3.3 | 3.2 | 3.3 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
|  | Bmax | [m] | 10 | 8.8 | 7.8 | 7.2 | 8.2 | 7.1 | 6.3 | 5.7 | 6.7 | 5.6 | 5 | 4.5
| Long (L) | Lmin | [m] | 4.4 | 4.3 | 4.3 | 4.2 | 4.3 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
|  | Lmax | [m] | 13.1 | 11.4 | 10.2 | 9.4 | 10.7 | 9.3 | 8.2 | 7.4 | 8.7 | 7.4 | 6.5 | 5.9
|  | Bmin | [m] | 2.6 | 2.5 | 2.5 | 2.5 | 2.5 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
|  | Bmax | [m] | 7.6 | 6.6 | 5.9 | 5.4 | 6.2 | 5.4 | 4.8 | 4.3 | 5 | 4.3 | 3.8 | 3.4
Mean Room Air Velocity |  | v | [m/s] | 0.16 | 0.16 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
Mean Draught Rating |  | DR | [%] | 15.4% | 14.9% | 14.6% | 14.5% | 14.7% | 14.5% | 14.4% | 14.4% | 14.5% | 14.4% | 14.4% | 14.3%
Mean PPD |  | PPD | [%] | 8% | 7.8% | 7.7% | 7.7% | 7.8% | 7.7% | 7.7% | 7.6% | 7.7% | 7.6% | 7.6% | 7.6%
Satisfies PPD Category (ISO7730) | bar: DN600 1 to DN1500 4
¦PMV¦ (ISO7730 & Ashrae Std 55) |  |  |  | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4
Product Selection & Code Generator
|  |  |  | DN600 |  |  |  | DN950 |  |  |  | DN1500
| Select a model to create product code | [15 empty] | for custom sizes refer to 'Bespoke' Sheet
|  |  |  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 |  | for return air grille please contact Smartair Diffusion
| Throw Setting |  |  | 2: short; 4: medium*; 2: long
| Discharge Direction (in direction of airflow) |  |  | 2: left; 4: centre*; 2: right
| Colour |  |  | 2: RAL9003* (signal white); 2: RAL9005 (jet black); 1: other
| Accessories |  |  | 2: Diffuser Only *; 4: With connection box and VCD (coming late 2020); 3: * indicates standard/default option
| Product Code |  |  | 1: Please select a valid size (Row 59)
|  |  |  | 2: click here to see product on smartair.asia |  |  |  |  | Copyright © 2020 SMARTAIR DIFFUSION
Group Box 28
Group Box 32
Group Box 36
Group Box 43
Group Box 47
Group Box 53
Group Box 64

## PMW-AD DN Eqns (hidden)
Inputs
|  |  | L/s | m³/h
|  |  | L/s/m² | m³/h/m² | ²
Airflow Rate Input | 120 | L/s | [L/s]
Selection | 1 | L/s/m² | [L/s/m²]
Mutiplier | 1
Selected Spec Flow | 9.8
Inputs
Airflow Rate Converted | 120
Turndown % | 1
Turndown Flow rate | 120
Max Total Pressure | 30
Height | 2.5
dT (cooling) | 12 | uses 8K for values between 0 to 8
ADPI | 90%
ADPI-Velocity Chart
95% | 0.2
90% | 0.25
80% | 0.29
70% | 0.33
Target Velocity | 0.25 | m/s
Area Type | 1
Selected L | 5.2
Selected B | 3.5
Type 2 Selected Area | 18.2 | Type 2 Spec Flow | 6.6 | L/s/m²
Converted Spec Flow | 9.8
Area from spec flow | 12.2449 | m2 | 12.2
Room Temp | 23
Factors
K.l.min | 7
K.l.max | 21
K.dT | 1 | -12 K / dT
K.H.min(sp) | 0.99994 | Increased draught risk as height increases, Fig 8, Krantz Layout Criteria TB 69 E | [6 empty] | 1.0037 | <old K.H.min
K.H.max(vol) | 1 | Reduce max throw with height to maintain constant volume to prevent stagnation
K.2D/3D | 1.1597 | Fig 8 / Fig 7 @ 0.25, Krantz Layout Criteria TB 69 E
v.room ≤ | 0.25 | m/s, Krantz Layout Criteria TB 69 E |  |  |  | 0.23665 | < old velocity at 90%adpi
K.adpi | 1.0035 | Adjustment factor for ADPI
K.h.min | 1.9
Target Q'' from ADPI
H | Ax | ^B | Q"
2.7 | 2876.0549 | 2.1519 | 145.6158
4 | 2647.6465 | 2.1753 | 129.7716
10 | 2313.9065 | 2.1944 | 110.451
2.5 | 175.9482 | -0.20487 | 145.8334
Q to v conversion
H | Aq | q^b
2.7 | 0.0247 | 0.4647 |  |  |  | 1.6552 | 120
4 | 0.0267 | 0.4597 |  |  |  | 3 | 161.5525
10 | 0.0293 | 0.4557
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Rows (Height) | Hr | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Neck Width | Wn | 577 | 577 | 577 | 577 | 915 | 915 | 915 | 915 | 1455 | 1455 | 1455 | 1455
Neck Height | Hn | 99 | 138 | 177 | 216 | 99 | 138 | 177 | 216 | 99 | 138 | 177 | 216
Face Width | Wf | 612 | 612 | 612 | 612 | 950 | 950 | 950 | 950 | 1490 | 1490 | 1490 | 1490
Face Height | Hf | 134 | 173 | 212 | 251 | 134 | 173 | 212 | 251 | 134 | 173 | 212 | 251
Total Pressure @ | Pt | 52.7511 | 26.8774 | 16.2157 | 10.8234 | 20.6868 | 10.5402 | 6.3591 | 4.2445 | 8.0673 | 4.1104 | 2.4799 | 1.6552
Min Flow Rate @ -12 | V min | 28.7 | 40.1 | 51.38 | 62.7 | 45.6 | 63.52 | 81.48 | 99.42 | 72.47 | 101.01 | 129.56 | 158.11
Min Flow Rate @ dT |  | 28.7 | 40.1 | 51.38 | 62.7 | 45.6 | 63.52 | 81.48 | 99.42 | 72.47 | 101.01 | 129.56 | 158.11
Sound Power Level | Lw | 50.7107 | 41.5215 | 34.6353 | 29.126 | 37.9539 | 28.7647 | 21.8785 | 16.3692 | 25.1209 | 15.9317 | 9.0455 | 3.5362
Sound Pressure Level | Lp* | 35.7107 | 26.5215 | 19.6353 | 14.126 | 22.9539 | 13.7647 | 6.8785 | 1.3692 | 10.1209 | 0.9317 | -5.9545 | -11.4638
Min Recommended Height | Hmin | 2.391 | 2.391 | 2.391 | 2.391 | 2.2466 | 2.2466 | 2.2466 | 2.2466 | 2.1551 | 2.1551 | 2.1551 | 2.1551
100% Airflow
L,W Vsp.min |  | 3.3861 | 3.2954 | 3.2581 | 3.2392 | 3.2737 | 3.2382 | 3.2235 | 3.2161 | 3.2295 | 3.2157 | 3.2099 | 3.2071
L,W Vsp.max |  | 11.0356 | 8.7613 | 7.8241 | 7.3501 | 8.2171 | 7.3252 | 6.9576 | 6.7718 | 7.1078 | 6.76 | 6.6166 | 6.5441
L,W throw max |  | 10.0352 | 8.9619 | 7.9132 | 7.1633 | 8.4023 | 7.1167 | 6.2839 | 5.6884 | 6.6631 | 5.6436 | 4.9832 | 4.511
Medium (M) | Lmin | 3.3861 | 3.2954 | 3.2581 | 3.2392 | 3.2737 | 3.2382 | 3.2235 | 3.2161 | 3.2295 | 3.2157 | 3.2099 | 3.2071
| Lmax | 10.0352 | 8.7613 | 7.8241 | 7.1633 | 8.2171 | 7.1167 | 6.2839 | 5.6884 | 6.6631 | 5.6436 | 4.9832 | 4.511
| Bmin | 3.3861 | 3.2954 | 3.2581 | 3.2392 | 3.2737 | 3.2382 | 3.2235 | 3.2161 | 3.2295 | 3.2157 | 3.2099 | 3.2071
| Bmax | 10.0352 | 8.7613 | 7.8241 | 7.1633 | 8.2171 | 7.1167 | 6.2839 | 5.6884 | 6.6631 | 5.6436 | 4.9832 | 4.511
L Vsp.min |  | 2.5735 | 2.5046 | 2.4762 | 2.4619 | 2.4881 | 2.4611 | 2.45 | 2.4443 | 2.4545 | 2.444 | 2.4396 | 2.4374
L Vsp.max |  | 8.3874 | 6.6588 | 5.9465 | 5.5862 | 6.2452 | 5.5673 | 5.288 | 5.1467 | 5.4021 | 5.1377 | 5.0288 | 4.9737
L throw max |  | 7.627 | 6.8113 | 6.0142 | 5.4443 | 6.386 | 5.4089 | 4.7759 | 4.3233 | 5.0641 | 4.2893 | 3.7874 | 3.4284
W Vsp.min |  | 4.4591 | 4.3397 | 4.2905 | 4.2656 | 4.3111 | 4.2643 | 4.245 | 4.2352 | 4.2529 | 4.2346 | 4.2271 | 4.2233
W Vsp.max |  | 14.5326 | 11.5375 | 10.3033 | 9.6791 | 10.8209 | 9.6463 | 9.1623 | 8.9175 | 9.3601 | 8.902 | 8.7133 | 8.6178
W throw max |  | 13.2151 | 11.8017 | 10.4207 | 9.4332 | 11.0648 | 9.3718 | 8.2751 | 7.4909 | 8.7745 | 7.4319 | 6.5623 | 5.9404
Short (S) | Lmin | 2.5735 | 2.5046 | 2.4762 | 2.4619 | 2.4881 | 2.4611 | 2.45 | 2.4443 | 2.4545 | 2.444 | 2.4396 | 2.4374
| Lmax | 7.627 | 6.6588 | 5.9465 | 5.4443 | 6.2452 | 5.4089 | 4.7759 | 4.3233 | 5.0641 | 4.2893 | 3.7874 | 3.4284
| Bmin | 4.4591 | 4.3397 | 4.2905 | 4.2656 | 4.3111 | 4.2643 | 4.245 | 4.2352 | 4.2529 | 4.2346 | 4.2271 | 4.2233
| Bmax | 13.2151 | 11.5375 | 10.3033 | 9.4332 | 10.8209 | 9.3718 | 8.2751 | 7.4909 | 8.7745 | 7.4319 | 6.5623 | 5.9404
L Vsp.min |  | 4.4202 | 4.3019 | 4.2531 | 4.2284 | 4.2735 | 4.2271 | 4.208 | 4.1983 | 4.2158 | 4.1977 | 4.1903 | 4.1865
L Vsp.max |  | 14.4059 | 11.4369 | 10.2135 | 9.5948 | 10.7266 | 9.5623 | 9.0825 | 8.8398 | 9.2785 | 8.8245 | 8.6374 | 8.5427
L throw max |  | 13.1 | 11.6989 | 10.3299 | 9.351 | 10.9684 | 9.2901 | 8.203 | 7.4256 | 8.6981 | 7.3672 | 6.5051 | 5.8886
W Vsp.min |  | 2.5616 | 2.493 | 2.4647 | 2.4504 | 2.4766 | 2.4497 | 2.4386 | 2.433 | 2.4431 | 2.4326 | 2.4283 | 2.4261
W Vsp.max |  | 8.3483 | 6.6278 | 5.9188 | 5.5602 | 6.2161 | 5.5414 | 5.2634 | 5.1228 | 5.377 | 5.1138 | 5.0054 | 4.9506
W throw max |  | 7.5915 | 6.7796 | 5.9863 | 5.419 | 6.3563 | 5.3837 | 4.7537 | 4.3032 | 5.0406 | 4.2693 | 3.7698 | 3.4125
Long (L) | Lmin | 4.4202 | 4.3019 | 4.2531 | 4.2284 | 4.2735 | 4.2271 | 4.208 | 4.1983 | 4.2158 | 4.1977 | 4.1903 | 4.1865
| Lmax | 13.1 | 11.4369 | 10.2135 | 9.351 | 10.7266 | 9.2901 | 8.203 | 7.4256 | 8.6981 | 7.3672 | 6.5051 | 5.8886
| Bmin | 2.5616 | 2.493 | 2.4647 | 2.4504 | 2.4766 | 2.4497 | 2.4386 | 2.433 | 2.4431 | 2.4326 | 2.4283 | 2.4261
| Bmax | 7.5915 | 6.6278 | 5.9188 | 5.419 | 6.2161 | 5.3837 | 4.7537 | 4.3032 | 5.0406 | 4.2693 | 3.7698 | 3.4125
VAV Turndown
Pressure |  | 52.7511 | 26.8774 | 16.2157 | 10.8234 | 20.6868 | 10.5402 | 6.3591 | 4.2445 | 8.0673 | 4.1104 | 2.4799 | 1.6552
L,W Vsp.min |  | 3.3861 | 3.2954 | 3.2581 | 3.2392 | 3.2737 | 3.2382 | 3.2235 | 3.2161 | 3.2295 | 3.2157 | 3.2099 | 3.2071
L,W Vsp.max |  | 11.0356 | 8.7613 | 7.8241 | 7.3501 | 8.2171 | 7.3252 | 6.9576 | 6.7718 | 7.1078 | 6.76 | 6.6166 | 6.5441
L,W throw max |  | 10.0352 | 8.9619 | 7.9132 | 7.1633 | 8.4023 | 7.1167 | 6.2839 | 5.6884 | 6.6631 | 5.6436 | 4.9832 | 4.511
Medium (M) | Lmin | 3.3861 | 3.2954 | 3.2581 | 3.2392 | 3.2737 | 3.2382 | 3.2235 | 3.2161 | 3.2295 | 3.2157 | 3.2099 | 3.2071
| Lmax | 10.0352 | 8.7613 | 7.8241 | 7.1633 | 8.2171 | 7.1167 | 6.2839 | 5.6884 | 6.6631 | 5.6436 | 4.9832 | 4.511
| Bmin | 3.3861 | 3.2954 | 3.2581 | 3.2392 | 3.2737 | 3.2382 | 3.2235 | 3.2161 | 3.2295 | 3.2157 | 3.2099 | 3.2071
| Bmax | 10.0352 | 8.7613 | 7.8241 | 7.1633 | 8.2171 | 7.1167 | 6.2839 | 5.6884 | 6.6631 | 5.6436 | 4.9832 | 4.511
L Vsp.min |  | 2.5735 | 2.5046 | 2.4762 | 2.4619 | 2.4881 | 2.4611 | 2.45 | 2.4443 | 2.4545 | 2.444 | 2.4396 | 2.4374
L Vsp.max |  | 8.3874 | 6.6588 | 5.9465 | 5.5862 | 6.2452 | 5.5673 | 5.288 | 5.1467 | 5.4021 | 5.1377 | 5.0288 | 4.9737
L throw max |  | 7.627 | 6.8113 | 6.0142 | 5.4443 | 6.386 | 5.4089 | 4.7759 | 4.3233 | 5.0641 | 4.2893 | 3.7874 | 3.4284
W Vsp.min |  | 4.4591 | 4.3397 | 4.2905 | 4.2656 | 4.3111 | 4.2643 | 4.245 | 4.2352 | 4.2529 | 4.2346 | 4.2271 | 4.2233
W Vsp.max |  | 14.5326 | 11.5375 | 10.3033 | 9.6791 | 10.8209 | 9.6463 | 9.1623 | 8.9175 | 9.3601 | 8.902 | 8.7133 | 8.6178
W throw max |  | 13.2151 | 11.8017 | 10.4207 | 9.4332 | 11.0648 | 9.3718 | 8.2751 | 7.4909 | 8.7745 | 7.4319 | 6.5623 | 5.9404
Short (S) | Lmin | 2.5735 | 2.5046 | 2.4762 | 2.4619 | 2.4881 | 2.4611 | 2.45 | 2.4443 | 2.4545 | 2.444 | 2.4396 | 2.4374
| Lmax | 7.627 | 6.6588 | 5.9465 | 5.4443 | 6.2452 | 5.4089 | 4.7759 | 4.3233 | 5.0641 | 4.2893 | 3.7874 | 3.4284
| Bmin | 4.4591 | 4.3397 | 4.2905 | 4.2656 | 4.3111 | 4.2643 | 4.245 | 4.2352 | 4.2529 | 4.2346 | 4.2271 | 4.2233
| Bmax | 13.2151 | 11.5375 | 10.3033 | 9.4332 | 10.8209 | 9.3718 | 8.2751 | 7.4909 | 8.7745 | 7.4319 | 6.5623 | 5.9404
L Vsp.min |  | 4.4202 | 4.3019 | 4.2531 | 4.2284 | 4.2735 | 4.2271 | 4.208 | 4.1983 | 4.2158 | 4.1977 | 4.1903 | 4.1865
L Vsp.max |  | 14.4059 | 11.4369 | 10.2135 | 9.5948 | 10.7266 | 9.5623 | 9.0825 | 8.8398 | 9.2785 | 8.8245 | 8.6374 | 8.5427
L throw max |  | 13.1 | 11.6989 | 10.3299 | 9.351 | 10.9684 | 9.2901 | 8.203 | 7.4256 | 8.6981 | 7.3672 | 6.5051 | 5.8886
W Vsp.min |  | 2.5616 | 2.493 | 2.4647 | 2.4504 | 2.4766 | 2.4497 | 2.4386 | 2.433 | 2.4431 | 2.4326 | 2.4283 | 2.4261
W Vsp.max |  | 8.3483 | 6.6278 | 5.9188 | 5.5602 | 6.2161 | 5.5414 | 5.2634 | 5.1228 | 5.377 | 5.1138 | 5.0054 | 4.9506
W throw max |  | 7.5915 | 6.7796 | 5.9863 | 5.419 | 6.3563 | 5.3837 | 4.7537 | 4.3032 | 5.0406 | 4.2693 | 3.7698 | 3.4125
Long (L) | Lmin | 4.4202 | 4.3019 | 4.2531 | 4.2284 | 4.2735 | 4.2271 | 4.208 | 4.1983 | 4.2158 | 4.1977 | 4.1903 | 4.1865
| Lmax | 13.1 | 11.4369 | 10.2135 | 9.351 | 10.7266 | 9.2901 | 8.203 | 7.4256 | 8.6981 | 7.3672 | 6.5051 | 5.8886
| Bmin | 2.5616 | 2.493 | 2.4647 | 2.4504 | 2.4766 | 2.4497 | 2.4386 | 2.433 | 2.4431 | 2.4326 | 2.4283 | 2.4261
| Bmax | 7.5915 | 6.6278 | 5.9188 | 5.419 | 6.2161 | 5.3837 | 4.7537 | 4.3032 | 5.0406 | 4.2693 | 3.7698 | 3.4125
DISTANCE RESULT | [14 empty] | old @ 128 L/s 50% td , -12K
Short (S) | Lmin | 2.6 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.4 | 2.4 | 2.5 | 2.4 | 2.4 | 2.4 |  | 2.852 | 2.7656 | 2.73 | 2.712 | 2.7449 | 2.7111 | 2.6971 | 2.69 | 2.7028 | 2.6896 | 2.6841 | 2.6814
| Lmax | 7.6 | 6.7 | 5.9 | 5.4 | 6.2 | 5.4 | 4.8 | 4.3 | 5.1 | 4.3 | 3.8 | 3.4 |  | 4.0249 | 3.4243 | 3.0236 | 2.737 | 3.2105 | 2.7192 | 2.401 | 2.1735 | 2.5459 | 2.1564 | 1.9041 | 1.7236
| Bmin | 4.5 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.2 | 4.2 | 4.3 | 4.2 | 4.2 | 4.2 |  | 4.9416 | 4.7919 | 4.7302 | 4.699 | 4.7561 | 4.6974 | 4.6732 | 4.6609 | 4.6831 | 4.6602 | 4.6507 | 4.646
| Bmax | 13.2 | 11.5 | 10.3 | 9.4 | 10.8 | 9.4 | 8.3 | 7.5 | 8.8 | 7.4 | 6.6 | 5.9 |  | 6.9738 | 5.9332 | 5.2389 | 4.7424 | 5.5627 | 4.7116 | 4.1602 | 3.766 | 4.4113 | 3.7363 | 3.2991 | 2.9865
Medium (M) | Lmin | 3.4 | 3.3 | 3.3 | 3.2 | 3.3 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 |  | 3.7525 | 3.6388 | 3.592 | 3.5683 | 3.6116 | 3.5671 | 3.5487 | 3.5394 | 3.5562 | 3.5388 | 3.5316 | 3.528
| Lmax | 10 | 8.8 | 7.8 | 7.2 | 8.2 | 7.1 | 6.3 | 5.7 | 6.7 | 5.6 | 5 | 4.5 |  | 5.2958 | 4.5055 | 3.9783 | 3.6013 | 4.2242 | 3.5778 | 3.1592 | 2.8598 | 3.3498 | 2.8373 | 2.5053 | 2.2678
| Bmin | 3.4 | 3.3 | 3.3 | 3.2 | 3.3 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 |  | 3.7525 | 3.6388 | 3.592 | 3.5683 | 3.6116 | 3.5671 | 3.5487 | 3.5394 | 3.5562 | 3.5388 | 3.5316 | 3.528
| Bmax | 10 | 8.8 | 7.8 | 7.2 | 8.2 | 7.1 | 6.3 | 5.7 | 6.7 | 5.6 | 5 | 4.5 |  | 5.2958 | 4.5055 | 3.9783 | 3.6013 | 4.2242 | 3.5778 | 3.1592 | 2.8598 | 3.3498 | 2.8373 | 2.5053 | 2.2678
Long (L) | Lmin | 4.4 | 4.3 | 4.3 | 4.2 | 4.3 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 |  | 4.8985 | 4.7501 | 4.689 | 4.6581 | 4.7146 | 4.6564 | 4.6325 | 4.6203 | 4.6423 | 4.6196 | 4.6102 | 4.6055
| Lmax | 13.1 | 11.4 | 10.2 | 9.4 | 10.7 | 9.3 | 8.2 | 7.4 | 8.7 | 7.4 | 6.5 | 5.9 |  | 6.9131 | 5.8815 | 5.1932 | 4.7011 | 5.5142 | 4.6705 | 4.124 | 3.7332 | 4.3728 | 3.7038 | 3.2704 | 2.9604
| Bmin | 2.6 | 2.5 | 2.5 | 2.5 | 2.5 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 |  | 2.8387 | 2.7527 | 2.7173 | 2.6994 | 2.7322 | 2.6984 | 2.6845 | 2.6775 | 2.6902 | 2.6771 | 2.6717 | 2.6689
| Bmax | 7.6 | 6.6 | 5.9 | 5.4 | 6.2 | 5.4 | 4.8 | 4.3 | 5 | 4.3 | 3.8 | 3.4 |  | 4.0062 | 3.4084 | 3.0095 | 2.7243 | 3.1955 | 2.7066 | 2.3899 | 2.1634 | 2.5341 | 2.1464 | 1.8952 | 1.7156
| Min Area | 11.7 | 10.75 | 10.75 | 10.75 | 10.75 | 10.75 | 10.08 | 10.08 | 10.75 | 10.08 | 10.08 | 10.08
| Max Area | 100.32 | 77.05 | 60.77 | 50.76 | 66.96 | 50.76 | 39.84 | 32.25 | 44.88 | 31.82 | 25.08 | 20.06
Short | Avg | 56.01 | 43.9 | 35.76 | 30.755 | 38.855 | 30.755 | 24.96 | 21.165 | 27.815 | 20.95 | 17.58 | 15.07
| Min Area | 11.56 | 10.89 | 10.89 | 10.24 | 10.89 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24 | 10.24
| Max Area | 100 | 77.44 | 60.84 | 51.84 | 67.24 | 50.41 | 39.69 | 32.49 | 44.89 | 31.36 | 25 | 20.25
Medium Avg Area | Avg | 55.78 | 44.165 | 35.865 | 31.04 | 39.065 | 30.325 | 24.965 | 21.365 | 27.565 | 20.8 | 17.62 | 15.245
| Min Area | 11.44 | 10.75 | 10.75 | 10.5 | 10.75 | 10.08 | 10.08 | 10.08 | 10.08 | 10.08 | 10.08 | 10.08
| Max Area | 99.56 | 75.24 | 60.18 | 50.76 | 66.34 | 50.22 | 39.36 | 31.82 | 43.5 | 31.82 | 24.7 | 20.06
Long Avg Area | Avg | 55.5 | 42.995 | 35.465 | 30.63 | 38.545 | 30.15 | 24.72 | 20.95 | 26.79 | 20.95 | 17.39 | 15.07
Avg-Avg Area |  |  | 43.6867 | 35.6967 | 30.8083 | 38.8217 | 30.41 | 24.8817 | 21.16 | 27.39 | 20.9
Average Area | 30.4172 | 0.4557 1 1: m2; 0.4557 2 2: Numbers for Display
Average area spec flow & format | 3.9451 | 0.4557 1 1: L/s/m2; 0.4557 2 2: 3.9
Selected Area | 30.4172 | bar: 0.4557 1 1
Selected Spec. Flow | 3.9451 | 0.4557 2 2: 3.9
Target W | 145.8334 | 0.4557 1 1: not used
Q'' Multiplier for v_avg to v_max at 30 Pa) |  | 0.4557 1 1: 1.1155; 0.4557 2 2: (not used in formulas but Discharge Velocity-Factor is based off this number)
Discharge Velocity - Factor |  | 1.1715 | 1.1092 | 1.0835 | 1.0705 | 1.0943 | 1.0698 | 1.0597 | 1.0546 | 1.0638 | 1.0543 | 1.0504 | 1.0484
W/m2 for selected area |  | 55.4621 | 52.5101 | 51.2937 | 50.6784 | 51.8038 | 50.6461 | 50.1691 | 49.9278 | 50.364 | 49.9125 | 49.7265 | 49.6324
| 2.7 | 0.15964 | 0.15563 | 0.15394 | 0.15308 | 0.15465 | 0.15304 | 0.15237 | 0.15203 | 0.15264 | 0.152 | 0.15174 | 0.15161
| 4 | 0.16913 | 0.16493 | 0.16317 | 0.16226 | 0.16391 | 0.16222 | 0.16151 | 0.16115 | 0.1618 | 0.16113 | 0.16085 | 0.16071
| 10 | 0.18264 | 0.17815 | 0.17626 | 0.17529 | 0.17705 | 0.17524 | 0.17448 | 0.1741 | 0.17479 | 0.17408 | 0.17378 | 0.17363
| Ax | 0.14573 | 0.14203 | 0.14048 | 0.13968 | 0.14113 | 0.13964 | 0.13902 | 0.13871 | 0.13928 | 0.13869 | 0.13844 | 0.13832
| B | 0.099479 | 0.09983 | 0.099981 | 0.10006 | 0.099917 | 0.10006 | 0.10012 | 0.10015 | 0.1001 | 0.10016 | 0.10018 | 0.10019
Mean Room Air Velocity (adj height) | 2.5 | 0.15962 | 0.15562 | 0.15394 | 0.15308 | 0.15465 | 0.15303 | 0.15236 | 0.15202 | 0.15264 | 0.152 | 0.15174 | 0.1516
Mean Draught Rating | DR | 0.1537 | 0.14859 | 0.14644 | 0.14534 | 0.14734 | 0.14529 | 0.14443 | 0.144 | 0.14478 | 0.14397 | 0.14364 | 0.14347
Mean PPD | PPD | 0.080239 | 0.078185 | 0.077332 | 0.076898 | 0.07769 | 0.076876 | 0.076539 | 0.076368 | 0.076677 | 0.076357 | 0.076226 | 0.076159
Satisfies PPD Category | (ISO7730) | bar: 0.4557 1 1 to 0.4557 12 4
PMV |  | 0.39092 | 0.37558 | 0.369 | 0.3656 | 0.37178 | 0.36542 | 0.36275 | 0.3614 | 0.36385 | 0.36131 | 0.36026 | 0.35972
Satifies PMV |  | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
SELECTION CRITERIA | TRUE = SHADE
Column shade |  | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
Merged cell shade |  | 0.4557 1 1: FALSE; 0.4557 5 1: FALSE; 0.4557 9 1: FALSE
Max/Min Pressure |  | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
Min Flow |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
Hmin |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
Short (S) | Lmin | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
| Lmax | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
| Bmin | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
| Bmax | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
Medium (M) | Lmin | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
| Lmax | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
| Bmin | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
| Bmax | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
Long (L) | Lmin | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
| Lmax | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
| Bmin | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
| Bmax | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
Cell Shading
Short (S) |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
|  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
|  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
|  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
Medium (M) |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
|  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
|  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
|  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
Long (L) |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
|  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
|  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
|  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
SUMMARY
Collated
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| Rows (Height) | Hr |  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Neck | Width | Wn | [mm] | 577 | 577 | 577 | 577 | 915 | 915 | 915 | 915 | 1455 | 1455 | 1455 | 1455
| Height | Hn | [mm] | 99 | 138 | 177 | 216 | 99 | 138 | 177 | 216 | 99 | 138 | 177 | 216
Face | Width | Wf | [mm] | 612 | 612 | 612 | 612 | 950 | 950 | 950 | 950 | 1490 | 1490 | 1490 | 1490
| Height | Hf | [mm] | 134 | 173 | 212 | 251 | 134 | 173 | 212 | 251 | 134 | 173 | 212 | 251
| Total Pressure | Pt | [Pa] | 52.7511 | 26.8774 | 16.2157 | 10.8234 | 20.6868 | 10.5402 | 6.3591 | 4.2445 | 8.0673 | 4.1104 | 2.4799 | 1.6552
Min Flow |  |  | L/s | 28.7 | 40.1 | 51.38 | 62.7 | 45.6 | 63.52 | 81.48 | 99.42 | 72.47 | 101.01 | 129.56 | 158.11
| Sound Power Level | Lw | [dB(A)] | 50.7107 | 41.5215 | 34.6353 | 29.126 | 37.9539 | 28.7647 | 21.8785 | 16.3692 | 25.1209 | 15.9317 | 9.0455 | 3.5362
| Sound Pressure Level | Lp* | [NC] | 35.7107 | 26.5215 | 19.6353 | 14.126 | 22.9539 | 13.7647 | 6.8785 | 1.3692 | 10.1209 | 0.9317 | -5.9545 | -11.4638
| Min Diffuser Height | Hmin | [m] | 2.391 | 2.391 | 2.391 | 2.391 | 2.2466 | 2.2466 | 2.2466 | 2.2466 | 2.1551 | 2.1551 | 2.1551 | 2.1551
Throw Setting | Short (S) | Lmin | [m] | 2.6 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.4 | 2.4 | 2.5 | 2.4 | 2.4 | 2.4
|  | Lmax | [m] | 7.6 | 6.7 | 5.9 | 5.4 | 6.2 | 5.4 | 4.8 | 4.3 | 5.1 | 4.3 | 3.8 | 3.4
|  | Bmin | [m] | 4.5 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.2 | 4.2 | 4.3 | 4.2 | 4.2 | 4.2
|  | Bmax | [m] | 13.2 | 11.5 | 10.3 | 9.4 | 10.8 | 9.4 | 8.3 | 7.5 | 8.8 | 7.4 | 6.6 | 5.9
| Medium (M) (default) | Lmin | [m] | 3.4 | 3.3 | 3.3 | 3.2 | 3.3 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
|  | Lmax | [m] | 10 | 8.8 | 7.8 | 7.2 | 8.2 | 7.1 | 6.3 | 5.7 | 6.7 | 5.6 | 5 | 4.5
|  | Bmin | [m] | 3.4 | 3.3 | 3.3 | 3.2 | 3.3 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
|  | Bmax | [m] | 10 | 8.8 | 7.8 | 7.2 | 8.2 | 7.1 | 6.3 | 5.7 | 6.7 | 5.6 | 5 | 4.5
| Long (L) | Lmin | [m] | 4.4 | 4.3 | 4.3 | 4.2 | 4.3 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
|  | Lmax | [m] | 13.1 | 11.4 | 10.2 | 9.4 | 10.7 | 9.3 | 8.2 | 7.4 | 8.7 | 7.4 | 6.5 | 5.9
|  | Bmin | [m] | 2.6 | 2.5 | 2.5 | 2.5 | 2.5 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
|  | Bmax | [m] | 7.6 | 6.6 | 5.9 | 5.4 | 6.2 | 5.4 | 4.8 | 4.3 | 5 | 4.3 | 3.8 | 3.4
| Mean Room Air Velocity | v | [m/s] | 0.15962 | 0.15562 | 0.15394 | 0.15308 | 0.15465 | 0.15303 | 0.15236 | 0.15202 | 0.15264 | 0.152 | 0.15174 | 0.1516
| Mean Draught Rating | DR | [%] | 0.1537 | 0.14859 | 0.14644 | 0.14534 | 0.14734 | 0.14529 | 0.14443 | 0.144 | 0.14478 | 0.14397 | 0.14364 | 0.14347
| Mean PPD | PPD | [%] | 0.080239 | 0.078185 | 0.077332 | 0.076898 | 0.07769 | 0.076876 | 0.076539 | 0.076368 | 0.076677 | 0.076357 | 0.076226 | 0.076159
| Satisfies PPD Category | (ISO7730) | bar: 1 1 to 12 4
Satisfies PMV |  |  |  | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Numbers Format & units
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| Rows (Height) | Hr |  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Neck | Width | Wn | [mm] | 577 | 577 | 577 | 577 | 915 | 915 | 915 | 915 | 1455 | 1455 | 1455 | 1455
| Height | Hn | [mm] | 99 | 138 | 177 | 216 | 99 | 138 | 177 | 216 | 99 | 138 | 177 | 216
Face | Width | Wf | [mm] | 612 | 612 | 612 | 612 | 950 | 950 | 950 | 950 | 1490 | 1490 | 1490 | 1490
| Height | Hf | [mm] | 134 | 173 | 212 | 251 | 134 | 173 | 212 | 251 | 134 | 173 | 212 | 251
| Total Pressure | Pt | [Pa] | 52.8 | 26.9 | 16.2 | 10.8 | 20.7 | 10.5 | 6.4 | 4.2 | 8.1 | 4.1 | 2.5 | 1.7
| Min Flowrate |  | L/s | 28.7 | 40.1 | 51.4 | 62.7 | 45.6 | 63.5 | 81.5 | 99.4 | 72.5 | 101 | 129.6 | 158.1
| Sound Power Level | Lw | [dB(A)] | 50.7 | 41.5 | 34.6 | 29.1 | 38 | 28.8 | 21.9 | 16.4 | 25.1 | 15.9 | 9 | 3.5
| Sound Pressure Level | Lp* | [NC] | 35.7 | 26.5 | 19.6 | 14.1 | 23 | 13.8 | 6.9 | 1.4 | 10.1 | 0.9 | -6 | -11.5
| Min Diffuser Height | Hmin | [m] | 2.4 | 2.4 | 2.4 | 2.4 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2
Throw Setting | Short (S) | Lmin | [m] | 2.6 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.4 | 2.4 | 2.5 | 2.4 | 2.4 | 2.4
|  | Lmax | [m] | 7.6 | 6.7 | 5.9 | 5.4 | 6.2 | 5.4 | 4.8 | 4.3 | 5.1 | 4.3 | 3.8 | 3.4
|  | Bmin | [m] | 4.5 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.2 | 4.2 | 4.3 | 4.2 | 4.2 | 4.2
|  | Bmax | [m] | 13.2 | 11.5 | 10.3 | 9.4 | 10.8 | 9.4 | 8.3 | 7.5 | 8.8 | 7.4 | 6.6 | 5.9
| Medium (M) (default) | Lmin | [m] | 3.4 | 3.3 | 3.3 | 3.2 | 3.3 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
|  | Lmax | [m] | 10 | 8.8 | 7.8 | 7.2 | 8.2 | 7.1 | 6.3 | 5.7 | 6.7 | 5.6 | 5 | 4.5
|  | Bmin | [m] | 3.4 | 3.3 | 3.3 | 3.2 | 3.3 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
|  | Bmax | [m] | 10 | 8.8 | 7.8 | 7.2 | 8.2 | 7.1 | 6.3 | 5.7 | 6.7 | 5.6 | 5 | 4.5
| Long (L) | Lmin | [m] | 4.4 | 4.3 | 4.3 | 4.2 | 4.3 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
|  | Lmax | [m] | 13.1 | 11.4 | 10.2 | 9.4 | 10.7 | 9.3 | 8.2 | 7.4 | 8.7 | 7.4 | 6.5 | 5.9
|  | Bmin | [m] | 2.6 | 2.5 | 2.5 | 2.5 | 2.5 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
|  | Bmax | [m] | 7.6 | 6.6 | 5.9 | 5.4 | 6.2 | 5.4 | 4.8 | 4.3 | 5 | 4.3 | 3.8 | 3.4
| Mean Room Air Velocity | v | [m/s] | 0.16 | 0.16 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
| Mean Draught Rating | DR | [%] | 0.154 | 0.149 | 0.146 | 0.145 | 0.147 | 0.145 | 0.144 | 0.144 | 0.145 | 0.144 | 0.144 | 0.143
| Mean PPD | PPD | [%] | 0.08 | 0.078 | 0.077 | 0.077 | 0.078 | 0.077 | 0.077 | 0.076 | 0.077 | 0.076 | 0.076 | 0.076
| Satisfies PPD Category | (ISO7730) | bar: 1 1 to 12 4
Satisfies PMV |  |  |  | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4
Results Format
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| Rows (Height) | Hr |  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
Neck | Width | Wn | [mm] | 577 | 577 | 577 | 577 | 915 | 915 | 915 | 915 | 1455 | 1455 | 1455 | 1455
| Height | Hn | [mm] | 99 | 138 | 177 | 216 | 99 | 138 | 177 | 216 | 99 | 138 | 177 | 216
Face | Width | Wf | [mm] | 612 | 612 | 612 | 612 | 950 | 950 | 950 | 950 | 1490 | 1490 | 1490 | 1490
| Height | Hf | [mm] | 134 | 173 | 212 | 251 | 134 | 173 | 212 | 251 | 134 | 173 | 212 | 251
| Total Pressure | Pt | [Pa] | 52.8 | 26.9 | 16.2 | 10.8 | 20.7 | 10.5 | 6.4 | 4.2 | 8.1 | 4.1 | < 3 | < 3
| Min Flow |  |  | 28.7 | 40.1 | 51.4 | 62.7 | 45.6 | 63.5 | 81.5 | 99.4 | 72.5 | 101 | 129.6 | 158.1
| Sound Power Level | Lw | [dB(A)] | 50.7 | 41.5 | 34.6 | 29.1 | 38 | 28.8 | 21.9 | 16.4 | 25.1 | 15.9 | < 15 | < 15
| Sound Pressure Level | Lp* | [NC] | 35.7 | 26.5 | 19.6 | 14.1 | 23 | 13.8 | 6.9 | < 5 | 10.1 | < 5 | < 5 | < 5
| Min Diffuser Height | Hmin | [m] | 2.4 | 2.4 | 2.4 | 2.4 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2
Throw Setting | Short (S) | Lmin | [m] | 2.6 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.4 | 2.4 | 2.5 | 2.4 | 2.4 | 2.4
|  | Lmax | [m] | 7.6 | 6.7 | 5.9 | 5.4 | 6.2 | 5.4 | 4.8 | 4.3 | 5.1 | 4.3 | 3.8 | 3.4
|  | Bmin | [m] | 4.5 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.2 | 4.2 | 4.3 | 4.2 | 4.2 | 4.2
|  | Bmax | [m] | 13.2 | 11.5 | 10.3 | 9.4 | 10.8 | 9.4 | 8.3 | 7.5 | 8.8 | 7.4 | 6.6 | 5.9
| Medium (M) (default) | Lmin | [m] | 3.4 | 3.3 | 3.3 | 3.2 | 3.3 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
|  | Lmax | [m] | 10 | 8.8 | 7.8 | 7.2 | 8.2 | 7.1 | 6.3 | 5.7 | 6.7 | 5.6 | 5 | 4.5
|  | Bmin | [m] | 3.4 | 3.3 | 3.3 | 3.2 | 3.3 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
|  | Bmax | [m] | 10 | 8.8 | 7.8 | 7.2 | 8.2 | 7.1 | 6.3 | 5.7 | 6.7 | 5.6 | 5 | 4.5
| Long (L) | Lmin | [m] | 4.4 | 4.3 | 4.3 | 4.2 | 4.3 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
|  | Lmax | [m] | 13.1 | 11.4 | 10.2 | 9.4 | 10.7 | 9.3 | 8.2 | 7.4 | 8.7 | 7.4 | 6.5 | 5.9
|  | Bmin | [m] | 2.6 | 2.5 | 2.5 | 2.5 | 2.5 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
|  | Bmax | [m] | 7.6 | 6.6 | 5.9 | 5.4 | 6.2 | 5.4 | 4.8 | 4.3 | 5 | 4.3 | 3.8 | 3.4
| Mean Room Air Velocity | v | [m/s] | 0.16 | 0.16 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
| Mean Draught Rating | DR | [%] | 0.154 | 0.149 | 0.146 | 0.145 | 0.147 | 0.145 | 0.144 | 0.144 | 0.145 | 0.144 | 0.144 | 0.143
| Mean PPD | PPD | [%] | 0.08 | 0.078 | 0.077 | 0.077 | 0.078 | 0.077 | 0.077 | 0.076 | 0.077 | 0.076 | 0.076 | 0.076
| Satisfies PPD Category | (ISO7730) | bar: 1 1 to 12 4
| PMV |  |  | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4 | ≤ 0.4

## PMW-DN-selection (hidden)
ADPI | [7 empty] | Radio | Rows | Model
95% | [7 empty] | 1 | 1 | 600
90% | [7 empty] | 2 | 2 | 600
80% | [7 empty] | 3 | 3 | 600
70% | [7 empty] | 4 | 4 | 600
[8 empty] | 5 | 1 | 950
Order Nominal | [7 empty] | 6 | 2 | 950
Rows | 3 | 7 | [5 empty] | 7 | 3 | 950
Model | 950 | [6 empty] | 8 | 4 | 950
Throw Setting | M | 2 | Medium |  |  |  |  | 9 | 1 | 1500
Discharge Direction (along airstream) | C | 2 | Centre |  |  |  |  | 10 | 2 | 1500
Damper | 0 | 1 | [5 empty] | 11 | 3 | 1500
Colour | RAL9003 | 1 | RAL9003 (signal white) |  |  |  |  | 12 | 4 | 1500
code |  | length | rows | throw | direction | colour
| SMARTEMP PMW-AD- | DN950- | 3- | TM- | C- | RAL9003
SMARTEMP PMW-AD-DN950-3-TM-C-RAL9003
Diffuser Height | 2.5
Order Bespoke
Rows | 1 | 0
Model | #VALUE!
Throw Setting | M | 2 | Medium
Discharge Direction (along airstream) | C | 2 | Centre
Damper | -1 | 0
Colour | RAL9003 | 1 | RAL9003 (signal white)
code |  | length | rows | throw | direction | colour
| SMARTEMP PMW-AD- | #VALUE! | 1- | TM- | C- | RAL9003
#VALUE!
diffuser height | 2.5
DN SIZE
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| Diffuser Size DN950 with | 2.6 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.4 | 2.4 | 2.5 | 2.4 | 2.4 | 2.4
| 2 | 7.6 | 6.7 | 5.9 | 5.4 | 6.2 | 5.4 | 4.8 | 4.3 | 5.1 | 4.3 | 3.8 | 3.4
| 3 | 4.5 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.2 | 4.2 | 4.3 | 4.2 | 4.2 | 4.2
| 4 | 13.2 | 11.5 | 10.3 | 9.4 | 10.8 | 9.4 | 8.3 | 7.5 | 8.8 | 7.4 | 6.6 | 5.9
| 5 | 3.4 | 3.3 | 3.3 | 3.2 | 3.3 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
| 6 | 10 | 8.8 | 7.8 | 7.2 | 8.2 | 7.1 | 6.3 | 5.7 | 6.7 | 5.6 | 5 | 4.5
| 7 | 3.4 | 3.3 | 3.3 | 3.2 | 3.3 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
| 8 | 10 | 8.8 | 7.8 | 7.2 | 8.2 | 7.1 | 6.3 | 5.7 | 6.7 | 5.6 | 5 | 4.5
| 9 | 4.4 | 4.3 | 4.3 | 4.2 | 4.3 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
| 10 | 13.1 | 11.4 | 10.2 | 9.4 | 10.7 | 9.3 | 8.2 | 7.4 | 8.7 | 7.4 | 6.5 | 5.9
| 11 | 2.6 | 2.5 | 2.5 | 2.5 | 2.5 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
| 12 | 7.6 | 6.6 | 5.9 | 5.4 | 6.2 | 5.4 | 4.8 | 4.3 | 5 | 4.3 | 3.8 | 3.4
| Model Select | 1: 7
| 2 | 1: 2.4
| 3 | 1: 4.8
| 4 | 1: 4.2
s | 5 | 1: 8.3
| 6 | 1: 3.2
| 7 | 1: 6.3
| 8 | 1: 3.2
m | 9 | 1: 6.3
| 10 | 1: 4.2
| 11 | 1: 8.2
| 12 | 1: 2.4
l | 13 | 1: 4.8
throw
| 6 | 1: 7; 2: 8; 3: 9
| lmin | 1: lmax; 2: bmin; 3: bmax
| 3.2 | 1: 6.3; 2: 3.2; 3: 6.3
DN BESPOKE
| 2 | 1: < 5
| 3 | 1: 2.1
| 4 | 1: 0.7
| 5 | 1: 0.9
| 6 | 1: 1.3
| 7 | 1: 1.6
| 8 | 1: 0.9
| 9 | 1: 1.2
| 10 | 1: 0.9
| 11 | 1: 1.2
| 12 | 1: 1.2
| 13 | 1: 1.6
throw
| 6 | 1: 7; 2: 8; 3: 9
| lmin | 1: lmax; 2: bmin; 3: bmax
| 1.3 | 1: 1.6; 2: 0.9; 3: 1.2
Order Code for DN Sizes
Size Radio | 0
Radio | Model | 1: Rows
0 | 0 | 1: 0
1 | 600 | bar: 1
2 | 600 | 1: 2
3 | 600 | 1: 3
4 | 600 | 1: 4
5 | 950 | bar: 1
6 | 950 | 1: 2
7 | 950 | 1: 3
8 | 950 | 1: 4
9 | 1500 | bar: 1
10 | 1500 | 1: 2
11 | 1500 | 1: 3
12 | 1500 | 1: 4
Selection | 0 | 1: 0
Text | DN0-0
Text | DN0 with 0 rows
Neck Dimensions | Neck [mm] mm × [mm] mm
Face Dimensions | Face [mm] mm × [mm] mm
Throw Setting
Throw setting radio | 2
| Code | 1: Description
1 | TS | 1: Short
2 | TM | 1: Medium
3 | TL | 1: Long
Select | TM | 1: Medium
Discharge direction
Discharge select | 2
| Code | 1: Description
1 | L | 1: Left
2 | C | 1: Centre
3 | R | 1: Right
Select | C | 1: Centre
Colour
Colour selection | 1
| Code | 1: Description
1 | RAL9003 | 1: Signal White
2 | RAL9005 | 1: Jet Black
3 | <colour> | 1: custom colour
Select | RAL9003 | 1: Signal White; 2: Signal White (RAL9003)
Accessories
Accessory select | 1
| Code | 1: Description
1 | 0 | 1: Diffuser only (no accessories)
2 | K | 1: With insulated connection box
Select | 0 | 1: Diffuser only (no accessories)
Description
Diffuser size DN0 with 0 row(s)
Throw distance set to medium
Centre discharge in direction of airstream
Face painted to Signal White (RAL9003)
| DN0-0- | 1: TM-; 2: C-; 3: RAL9003-; 4: 0
Order Code: | Please select a valid size (Row 59)
Results
PMW-AD-
1 | Rows (Height) | 2: 0
2 | Wn | 2: [mm]
3 | Hn | 2: [mm]
4 | Wf | 2: [mm]
5 | Hf | 2: [mm]
6 | Total Pressure | 2: [Pa]
7 | Min Recommended Flow Rate | 2: 0
8 | Sound Power Level | 2: [dB(A)]
9 | Sound Pressure Level * | 2: [NC]
10 | Min Recommended Diffuser Height | 2: [m]
11 | S | 1: Lmin; 2: [m]
12 | S | 1: Lmax; 2: [m]
13 | S | 1: Bmin; 2: [m]
14 | S | 1: Bmax; 2: [m]
15 | M | 1: Lmin; 2: [m]
16 | M | 1: Lmax; 2: [m]
17 | M | 1: Bmin; 2: [m]
18 | M | 1: Bmax; 2: [m]
19 | L | 1: Lmin; 2: [m]
20 | L | 1: Lmax; 2: [m]
21 | L | 1: Bmin; 2: [m]
22 | L | 1: Bmax; 2: [m]
23 | Mean Room Air Velocity | 2: [m/s]
24 | Mean Draught Rating | 2: [%]
25 | Mean PPD | 2: [%]
26 | Satisfies PPD Category | 2: 0; 4: Δ
27 | PMV | 2: 0
Multiplier | 1
Main Page
Airflow | 120 | 1: L/s; 2: L/s/m²
TD to | 100
min flow | 120
dt | -12
height | 2.5
spec flow | 3.9
Airflow Pressure | 120 L/s @ [Pa] Pa total
Min airflow | 120 L/s (VAV turndown to 100% )
Min Permissible Airflow | 0 L/s @ ΔT = -12 K
Acoustic
SWL | [dB(A)] dB(A)
SPL | [NC] NC (based on 10 dB room absorption)
Comfort for 3.9 L/s/m²
ADPI | 90%
Mean room air | [m/s] m/s
draught rating | #VALUE!
ppd | [%]
satisfies category | Category 0
PMV | -0 ≤ PMV ≤ +0 | 1: 0
Throw Selection
selection | Medium throw selected
selected height | 2.5 m selected install height
height | [m] m minimum recommended height
Lmin | [m]
Lmax | [m]
Bmin | [m]
Bmax | [m]
L | [m] m - [m] m
B | [m] m - [m] m

## PMW-AD DN600,950,1500 Summary
PMW-AD Performance Calculator Summary
Project | <Project Name>
Company | <Name>
Consultant | <Name>
Product | SMARTEMP PMW-AD
Perforated Multistream Adjustable Wall Diffuser
Size | DN0 with 0 rows
Project Summary
Selected Airflow | 120 L/s @ [Pa] Pa total
Min Selected Airflow | 120 L/s (VAV turndown to 100% )
Min Recommended Airflow | 0 L/s @ ΔT = -12 K
Acoustic Performance
Sound Power Level | [dB(A)] dB(A)
Sound Pressure Level | [NC] NC (based on 10 dB room absorption)
Recommended Layout
Medium throw selected
2.5 m selected install height
Comfort for 3.9 L/s/m²
ADPI | 90%
Mean Room Air Velocity | [m/s] m/s
Draught Rating (DR) | #VALUE!
Mean PPD | [%]
Satisfies PPD (ISO7730) | Category 0
Satisfies PMV * | -0 ≤ PMV ≤ +0 | * ISO7730; ASHRAE Std 55
Description | Diffuser size DN0 with 0 row(s)
Neck [mm] mm × [mm] mm
Face [mm] mm × [mm] mm
Throw distance set to medium
Centre discharge in direction of airstream
Face painted to Signal White (RAL9003)
Order Code | Please select a valid size (Row 59)
[m] m - [m] m
[m] m - [m] m
[m] m minimum recommended height

## DN600, DN950, DN1500 Calculator (hidden)
Units
Type | 2 |  | FACTORS: | K.l.min | 7 | [17 empty] | FACTORS: | K.l.min | 7 | [17 empty] | FACTORS: | K.l.min | 7
Multiplier | 3.6 |  |  | K.l.max | 21 | [18 empty] | K.l.max | 21 | [18 empty] | K.l.max | 21
Type | m³/h |  |  | K.dT | 1 | -12 K / dT | [17 empty] | K.dT | 1 | -12 K / dT | [17 empty] | K.dT | 1 | -12 K / dT
Type2 | m³/h/m² |  |  | K.H.min(sp) | 1.0037 | Increased draught risk as height increases, Fig 8, Krantz Layout Criteria TB 69 E | [17 empty] | K.H.min(sp) | 1.0037 | Increased draught risk as height increases, Fig 8, Krantz Layout Criteria TB 69 E | [17 empty] | K.H.min(sp) | 1.0037 | Increased draught risk as height increases, Fig 8, Krantz Layout Criteria TB 69 E
|  |  |  | K.H.max(vol) | 1 | Reduce max throw with height to maintain constant volume to prevent stagnation | [17 empty] | K.H.max(vol) | 1 | Reduce max throw with height to maintain constant volume to prevent stagnation | [17 empty] | K.H.max(vol) | 1 | Reduce max throw with height to maintain constant volume to prevent stagnation
|  |  |  | K.2D/3D | 1.1597 | Fig 8 / Fig 7 @ 0.25, Krantz Layout Criteria TB 69 E | [17 empty] | K.2D/3D | 1.1597 | Fig 8 / Fig 7 @ 0.25, Krantz Layout Criteria TB 69 E | [17 empty] | K.2D/3D | 1.1597 | Fig 8 / Fig 7 @ 0.25, Krantz Layout Criteria TB 69 E
|  |  |  | K.adpi | 0.94595 | Adjustment factor for ADPI | [17 empty] | K.adpi | 0.94595 | Adjustment factor for ADPI | [17 empty] | K.adpi | 0.94595 | Adjustment factor for ADPI
|  |  |  | v.room ≤ | 0.23665 | m/s, Krantz Layout Criteria TB 69 E | [17 empty] | v.room ≤ | 0.23665 | m/s, Krantz Layout Criteria TB 69 E | [17 empty] | v.room ≤ | 0.23665 | m/s, Krantz Layout Criteria TB 69 E
|  |  |  | K.h.min | 1.9 | [18 empty] | K.h.min | 1.9 | [18 empty] | K.h.min | 1.9
[25 empty] | INPUT | [19 empty] | INPUT
[24 empty] | H.diffuser = | 2.5 | m | [17 empty] | H.diffuser = | 2.5 | m
|  | PMW- | W.neck | [18 empty] | PMW- | W.neck | dT(cooling) = | -12 | K | [15 empty] | PMW- | W.neck | dT(cooling) = | -12 | K
|  | AD- | mm | [18 empty] | AD- | mm | ADPI ³ | 90 | % | [15 empty] | AD- | mm | ADPI ³ | 90 | %
|  | DN 600 | 577 | [18 empty] | DN 950 | 915 | = | 33.3333 | L/s | [15 empty] | DN 1500 | 1455 | = | 33.3333 | L/s
INPUT
|  |  |  | H.diffuser = | 2.5 | m |  |  |  | m |  |  |  |  | Height to Diffuser Centre-Line = 2.0 to 4.5 m
|  |  |  | dT(cooling) = | -12 | K |  |  |  | K |  |  |  |  | dT = -8 K to -12 K
|  |  |  | ADPI ³ | 90 | % |  |  |  | % |  |  |  |  | 70%, 80%, 90% or 95%
|  |  |  | = | 33.3333 | L/s |  |  |  | L/s
|  |  |  | PMW-AD- | DN600 | [18 empty] | PMW-AD- | DN950 | [18 empty] | PMW-AD- | DN1500
|  |  |  | W.n | 577 | mm | [17 empty] | W.n | 915 | mm | [17 empty] | W.n | 1455 | mm | [14 empty] | mm
|  |  |  | W.f | 612 | mm | [18 empty] | 950 | [19 empty] | 1490 | [15 empty] | mm
|  |  |  | Rows | 1 |  |  |  |  | 2 |  |  |  |  | 3 |  |  |  |  | 4 |  |  |  |  | 1 |  |  |  |  | 2 |  |  |  |  | 3 |  |  |  |  | 4 |  |  |  |  | 1 |  |  |  |  | 2 |  |  |  |  | 3 |  |  |  |  | 4
|  |  |  | H.c | 99 |  |  |  |  | 138 |  |  |  |  | 177 |  |  |  |  | 216 |  |  |  |  | 99 |  |  |  |  | 138 |  |  |  |  | 177 |  |  |  |  | 216 |  |  |  |  | 99 |  |  |  |  | 138 |  |  |  |  | 177 |  |  |  |  | 216 | mm
|  |  |  | H.f | 134 | 35 | 35 | 35 | 35 | 173 | 35 | 35 | 35 | 35 | 212 | 35 | 35 | 35 | 35 | 251 | 35 | 35 | 35 | 35 | 134 | 35 | 35 | 35 | 35 | 173 | 35 | 35 | 35 | 35 | 212 | 35 | 35 | 35 | 35 | 251 | 35 | 35 | 35 | 35 | 134 | 35 | 35 | 35 | 35 | 173 | 35 | 35 | 35 | 35 | 212 | 35 | 35 | 35 | 35 | 251 | mm
|  |  |  | Pt | 3.9158 | Pa |  |  | Pt | 1.9952 | Pa |  |  | Pt | 1.2037 | Pa |  |  | Pt | 0.80345 | Pa |  |  | Pt | 1.5356 | Pa |  |  | Pt | 0.78243 | Pa |  |  | Pt | 0.47205 | Pa |  |  | Pt | 0.31508 | Pa |  |  | Pt | 0.59885 | Pa |  |  | Pt | 0.30512 | Pa |  |  | Pt | 0.18409 | Pa |  |  | Pt | 0.12287 | Pa
|  | H.neck | Throw | Lw | <15 | dB(A) | H.neck | Discharge | Lw | <15 | dB(A) | H.neck | Discharge | Lw | <15 | dB(A) | H.neck | Discharge | Lw | <15 | dB(A) | H.neck | Discharge | Lw | <15 | dB(A) | H.neck | Discharge | Lw | <15 | dB(A) | H.neck | Discharge | Lw | <15 | dB(A) | H.neck | Discharge | Lw | <15 | dB(A) | H.neck | Discharge | Lw | <15 | dB(A) | H.neck | Discharge | Lw | <15 | dB(A) | H.neck | Discharge | Lw | <15 | dB(A) | H.neck | Discharge | Lw | <15 | dB(A)
|  | mm | Setting | Lp* | <5 | NC* | mm | Setting | Lp* | <5 | NC* | mm | Setting | Lp* | <5 | NC* | mm | Setting | Lp* | <5 | NC* | mm | Setting | Lp* | <5 | NC* | mm | Setting | Lp* | <5 | NC* | mm | Setting | Lp* | <5 | NC* | mm | Setting | Lp* | <5 | NC* | mm | Setting | Lp* | <5 | NC* | mm | Setting | Lp* | <5 | NC* | mm | Setting | Lp* | <5 | NC* | mm | Setting | Lp* | <5 | NC*
|  |  |  | L Vsp.min | 1.3714 |  |  |  | L Vsp.min | 1.3685 |  |  |  | L Vsp.min | 1.3673 |  |  |  | L Vsp.min | 1.3667 |  |  |  | L Vsp.min | 1.3678 |  |  |  | L Vsp.min | 1.3667 |  |  |  | L Vsp.min | 1.3662 |  |  |  | L Vsp.min | 1.366 |  |  |  | L Vsp.min | 1.3664 |  |  |  | L Vsp.min | 1.366 |  |  |  | L Vsp.min | 1.3658 |  |  |  | L Vsp.min | 1.3657
|  |  |  | L Vsp.max | 2.546 |  |  |  | L Vsp.max | 2.4823 |  |  |  | L Vsp.max | 2.456 |  |  |  | L Vsp.max | 2.4427 |  |  |  | L Vsp.max | 2.467 |  |  |  | L Vsp.max | 2.442 |  |  |  | L Vsp.max | 2.4317 |  |  |  | L Vsp.max | 2.4265 |  |  |  | L Vsp.max | 2.4359 |  |  |  | L Vsp.max | 2.4262 |  |  |  | L Vsp.max | 2.4222 |  |  |  | L Vsp.max | 2.4201
|  |  |  | L throw max | 2.1057 |  |  |  | L throw max | 1.7835 |  |  |  | L throw max | 1.5748 |  |  |  | L throw max | 1.4255 |  |  |  | L throw max | 1.6721 |  |  |  | L throw max | 1.4163 |  |  |  | L throw max | 1.2505 |  |  |  | L throw max | 1.132 |  |  |  | L throw max | 1.326 |  |  |  | L throw max | 1.1231 |  |  |  | L throw max | 0.99169 |  |  |  | L throw max | 0.89771
|  |  |  | W Vsp.min | 2.3761 |  |  |  | W Vsp.min | 2.3712 |  |  |  | W Vsp.min | 2.3691 |  |  |  | W Vsp.min | 2.3681 |  |  |  | W Vsp.min | 2.37 |  |  |  | W Vsp.min | 2.368 |  |  |  | W Vsp.min | 2.3672 |  |  |  | W Vsp.min | 2.3668 |  |  |  | W Vsp.min | 2.3675 |  |  |  | W Vsp.min | 2.3668 |  |  |  | W Vsp.min | 2.3665 |  |  |  | W Vsp.min | 2.3663
|  |  |  | W Vsp.max | 4.4114 |  |  |  | W Vsp.max | 4.301 |  |  |  | W Vsp.max | 4.2555 |  |  |  | W Vsp.max | 4.2325 |  |  |  | W Vsp.max | 4.2746 |  |  |  | W Vsp.max | 4.2312 |  |  |  | W Vsp.max | 4.2134 |  |  |  | W Vsp.max | 4.2044 |  |  |  | W Vsp.max | 4.2207 |  |  |  | W Vsp.max | 4.2038 |  |  |  | W Vsp.max | 4.1968 |  |  |  | W Vsp.max | 4.1933
|  |  |  | W throw max | 3.6484 |  |  |  | W throw max | 3.0902 |  |  |  | W throw max | 2.7286 |  |  |  | W throw max | 2.47 |  |  |  | W throw max | 2.8972 |  |  |  | W throw max | 2.4539 |  |  |  | W throw max | 2.1668 |  |  |  | W throw max | 1.9614 |  |  |  | W throw max | 2.2975 |  |  |  | W throw max | 1.946 |  |  |  | W throw max | 1.7183 |  |  |  | W throw max | 1.5554
|  |  |  | Hmin | 2.1297 | m |  |  | Hmin | 2.1297 | m |  |  | Hmin | 2.1297 | m |  |  | Hmin | 2.1297 | m |  |  | Hmin | 2.0818 | m |  |  | Hmin | 2.0818 | m |  |  | Hmin | 2.0818 | m |  |  | Hmin | 2.0818 | m |  |  | Hmin | 2.0514 | m |  |  | Hmin | 2.0514 | m |  |  | Hmin | 2.0514 | m |  |  | Hmin | 2.0514 | m
|  |  |  | Lmin | 1.3714 | m |  |  | Lmin | 1.3685 | m |  |  | Lmin | 1.3673 | m |  |  | Lmin | 1.3667 | m |  |  | Lmin | 1.3678 | m |  |  | Lmin | 1.3667 | m |  |  | Lmin | 1.3662 | m |  |  | Lmin | 1.366 | m |  |  | Lmin | 1.3664 | m |  |  | Lmin | 1.366 | m |  |  | Lmin | 1.3658 | m |  |  | Lmin | 1.3657 | m
|  |  | S | Lmax | 2.1057 | m |  | S | Lmax | 1.7835 | m |  | S | Lmax | 1.5748 | m |  | S | Lmax | 1.4255 | m |  | S | Lmax | 1.6721 | m |  | S | Lmax | 1.4163 | m |  | S | Lmax | 1.2505 | m |  | S | Lmax | 1.132 | m |  | S | Lmax | 1.326 | m |  | S | Lmax | 1.1231 | m |  | S | Lmax | 0.99169 | m |  | S | Lmax | 0.89771 | m
|  |  | Short | Wmin | 2.3761 | m |  | Short | Wmin | 2.3712 | m |  | Short | Wmin | 2.3691 | m |  | Short | Wmin | 2.3681 | m |  | Short | Wmin | 2.37 | m |  | Short | Wmin | 2.368 | m |  | Short | Wmin | 2.3672 | m |  | Short | Wmin | 2.3668 | m |  | Short | Wmin | 2.3675 | m |  | Short | Wmin | 2.3668 | m |  | Short | Wmin | 2.3665 | m |  | Short | Wmin | 2.3663 | m
|  |  |  | Wmax | 3.6484 | m |  |  | Wmax | 3.0902 | m |  |  | Wmax | 2.7286 | m |  |  | Wmax | 2.47 | m |  |  | Wmax | 2.8972 | m |  |  | Wmax | 2.4539 | m |  |  | Wmax | 2.1668 | m |  |  | Wmax | 1.9614 | m |  |  | Wmax | 2.2975 | m |  |  | Wmax | 1.946 | m |  |  | Wmax | 1.7183 | m |  |  | Wmax | 1.5554 | m
|  |  |  | L,W Vsp.min | 1.8044 |  |  |  | L,W Vsp.min | 1.8006 |  |  |  | L,W Vsp.min | 1.799 |  |  |  | L,W Vsp.min | 1.7983 |  |  |  | L,W Vsp.min | 1.7997 |  |  |  | L,W Vsp.min | 1.7982 |  |  |  | L,W Vsp.min | 1.7976 |  |  |  | L,W Vsp.min | 1.7973 |  |  |  | L,W Vsp.min | 1.7979 |  |  |  | L,W Vsp.min | 1.7973 |  |  |  | L,W Vsp.min | 1.797 |  |  |  | L,W Vsp.min | 1.7969
|  |  |  | L,W Vsp.max | 3.3499 |  |  |  | L,W Vsp.max | 3.2661 |  |  |  | L,W Vsp.max | 3.2315 |  |  |  | L,W Vsp.max | 3.214 |  |  |  | L,W Vsp.max | 3.246 |  |  |  | L,W Vsp.max | 3.2131 |  |  |  | L,W Vsp.max | 3.1995 |  |  |  | L,W Vsp.max | 3.1927 |  |  |  | L,W Vsp.max | 3.2051 |  |  |  | L,W Vsp.max | 3.1922 |  |  |  | L,W Vsp.max | 3.187 |  |  |  | L,W Vsp.max | 3.1843
|  |  |  | L,W throw max | 2.7705 |  |  |  | L,W throw max | 2.3466 |  |  |  | L,W throw max | 2.072 |  |  |  | L,W throw max | 1.8757 |  |  |  | L,W throw max | 2.2001 |  |  |  | L,W throw max | 1.8635 |  |  |  | L,W throw max | 1.6454 |  |  |  | L,W throw max | 1.4895 |  |  |  | L,W throw max | 1.7447 |  |  |  | L,W throw max | 1.4777 |  |  |  | L,W throw max | 1.3048 |  |  |  | L,W throw max | 1.1812
|  |  |  | Lmin | 1.8044 | m |  |  | Lmin | 1.8006 | m |  |  | Lmin | 1.799 | m |  |  | Lmin | 1.7983 | m |  |  | Lmin | 1.7997 | m |  |  | Lmin | 1.7982 | m |  |  | Lmin | 1.7976 | m |  |  | Lmin | 1.7973 | m |  |  | Lmin | 1.7979 | m |  |  | Lmin | 1.7973 | m |  |  | Lmin | 1.797 | m |  |  | Lmin | 1.7969 | m
|  | 99 | M | Lmax | 2.7705 | m | 138 | M | Lmax | 2.3466 | m | 177 | M | Lmax | 2.072 | m | 216 | M | Lmax | 1.8757 | m | 99 | M | Lmax | 2.2001 | m | 138 | M | Lmax | 1.8635 | m | 177 | M | Lmax | 1.6454 | m | 216 | M | Lmax | 1.4895 | m | 99 | M | Lmax | 1.7447 | m | 138 | M | Lmax | 1.4777 | m | 177 | M | Lmax | 1.3048 | m | 216 | M | Lmax | 1.1812 | m
|  | (1-row) | Medium | Wmin | 1.8044 | m | (2-row) | Medium | Wmin | 1.8006 | m | (3-row) | Medium | Wmin | 1.799 | m | (4-row) | Medium | Wmin | 1.7983 | m | (1-row) | Medium | Wmin | 1.7997 | m | (2-row) | Medium | Wmin | 1.7982 | m | (3-row) | Medium | Wmin | 1.7976 | m | (4-row) | Medium | Wmin | 1.7973 | m | (1-row) | Medium | Wmin | 1.7979 | m | (2-row) | Medium | Wmin | 1.7973 | m | (3-row) | Medium | Wmin | 1.797 | m | (4-row) | Medium | Wmin | 1.7969 | m
|  |  |  | Wmax | 2.7705 | m |  |  | Wmax | 2.3466 | m |  |  | Wmax | 2.072 | m |  |  | Wmax | 1.8757 | m |  |  | Wmax | 2.2001 | m |  |  | Wmax | 1.8635 | m |  |  | Wmax | 1.6454 | m |  |  | Wmax | 1.4895 | m |  |  | Wmax | 1.7447 | m |  |  | Wmax | 1.4777 | m |  |  | Wmax | 1.3048 | m |  |  | Wmax | 1.1812 | m
|  |  |  | L Vsp.min | 2.3554 |  |  |  | L Vsp.min | 2.3505 |  |  |  | L Vsp.min | 2.3485 |  |  |  | L Vsp.min | 2.3474 |  |  |  | L Vsp.min | 2.3493 |  |  |  | L Vsp.min | 2.3474 |  |  |  | L Vsp.min | 2.3466 |  |  |  | L Vsp.min | 2.3462 |  |  |  | L Vsp.min | 2.3469 |  |  |  | L Vsp.min | 2.3462 |  |  |  | L Vsp.min | 2.3459 |  |  |  | L Vsp.min | 2.3457
|  |  |  | L Vsp.max | 4.373 |  |  |  | L Vsp.max | 4.2635 |  |  |  | L Vsp.max | 4.2184 |  |  |  | L Vsp.max | 4.1956 |  |  |  | L Vsp.max | 4.2373 |  |  |  | L Vsp.max | 4.1944 |  |  |  | L Vsp.max | 4.1767 |  |  |  | L Vsp.max | 4.1677 |  |  |  | L Vsp.max | 4.1839 |  |  |  | L Vsp.max | 4.1672 |  |  |  | L Vsp.max | 4.1603 |  |  |  | L Vsp.max | 4.1568
|  |  |  | L throw max | 3.6166 |  |  |  | L throw max | 3.0633 |  |  |  | L throw max | 2.7048 |  |  |  | L throw max | 2.4485 |  |  |  | L throw max | 2.872 |  |  |  | L throw max | 2.4326 |  |  |  | L throw max | 2.1479 |  |  |  | L throw max | 1.9444 |  |  |  | L throw max | 2.2775 |  |  |  | L throw max | 1.929 |  |  |  | L throw max | 1.7033 |  |  |  | L throw max | 1.5419
|  |  |  | W Vsp.min | 1.365 |  |  |  | W Vsp.min | 1.3621 |  |  |  | W Vsp.min | 1.361 |  |  |  | W Vsp.min | 1.3604 |  |  |  | W Vsp.min | 1.3615 |  |  |  | W Vsp.min | 1.3603 |  |  |  | W Vsp.min | 1.3599 |  |  |  | W Vsp.min | 1.3596 |  |  |  | W Vsp.min | 1.3601 |  |  |  | W Vsp.min | 1.3596 |  |  |  | W Vsp.min | 1.3594 |  |  |  | W Vsp.min | 1.3593
|  |  |  | W Vsp.max | 2.5342 |  |  |  | W Vsp.max | 2.4707 |  |  |  | W Vsp.max | 2.4446 |  |  |  | W Vsp.max | 2.4314 |  |  |  | W Vsp.max | 2.4556 |  |  |  | W Vsp.max | 2.4307 |  |  |  | W Vsp.max | 2.4204 |  |  |  | W Vsp.max | 2.4152 |  |  |  | W Vsp.max | 2.4246 |  |  |  | W Vsp.max | 2.4149 |  |  |  | W Vsp.max | 2.4109 |  |  |  | W Vsp.max | 2.4089
|  |  |  | W throw max | 2.0959 |  |  |  | W throw max | 1.7752 |  |  |  | W throw max | 1.5675 |  |  |  | W throw max | 1.4189 |  |  |  | W throw max | 1.6643 |  |  |  | W throw max | 1.4097 |  |  |  | W throw max | 1.2447 |  |  |  | W throw max | 1.1268 |  |  |  | W throw max | 1.3198 |  |  |  | W throw max | 1.1179 |  |  |  | W throw max | 0.98708 |  |  |  | W throw max | 0.89354
|  |  |  | Lmin | 2.3554 | m |  |  | Lmin | 2.3505 | m |  |  | Lmin | 2.3485 | m |  |  | Lmin | 2.3474 | m |  |  | Lmin | 2.3493 | m |  |  | Lmin | 2.3474 | m |  |  | Lmin | 2.3466 | m |  |  | Lmin | 2.3462 | m |  |  | Lmin | 2.3469 | m |  |  | Lmin | 2.3462 | m |  |  | Lmin | 2.3459 | m |  |  | Lmin | 2.3457 | m
|  |  | L | Lmax | 3.6166 | m |  | L | Lmax | 3.0633 | m |  | L | Lmax | 2.7048 | m |  | L | Lmax | 2.4485 | m |  | L | Lmax | 2.872 | m |  | L | Lmax | 2.4326 | m |  | L | Lmax | 2.1479 | m |  | L | Lmax | 1.9444 | m |  | L | Lmax | 2.2775 | m |  | L | Lmax | 1.929 | m |  | L | Lmax | 1.7033 | m |  | L | Lmax | 1.5419 | m
|  |  | Long | Wmin | 1.365 | m |  | Long | Wmin | 1.3621 | m |  | Long | Wmin | 1.361 | m |  | Long | Wmin | 1.3604 | m |  | Long | Wmin | 1.3615 | m |  | Long | Wmin | 1.3603 | m |  | Long | Wmin | 1.3599 | m |  | Long | Wmin | 1.3596 | m |  | Long | Wmin | 1.3601 | m |  | Long | Wmin | 1.3596 | m |  | Long | Wmin | 1.3594 | m |  | Long | Wmin | 1.3593 | m
|  |  |  | Wmax | 2.0959 | m |  |  | Wmax | 1.7752 | m |  |  | Wmax | 1.5675 | m |  |  | Wmax | 1.4189 | m |  |  | Wmax | 1.6643 | m |  |  | Wmax | 1.4097 | m |  |  | Wmax | 1.2447 | m |  |  | Wmax | 1.1268 | m |  |  | Wmax | 1.3198 | m |  |  | Wmax | 1.1179 | m |  |  | Wmax | 0.98708 | m |  |  | Wmax | 0.89354 | m
[5 empty] | 1 |  |  |  |  | 2 |  |  |  |  | 3 |  |  |  |  | 4 |  |  |  |  | 5 |  |  |  |  | 6 |  |  |  |  | 7 |  |  |  |  | 8 |  |  |  |  | 9 |  |  |  |  | 10 |  |  |  |  | 11 |  |  |  |  | 12
[5 empty] | 92.2627 |  |  |  |  | 129.2553 |  |  |  |  | 166.4082 |  |  |  |  | 203.6859 |  |  |  |  | 147.3314 |  |  |  |  | 206.4036 |  |  |  |  | 265.7319 |  |  |  |  | 325.2595 |  |  |  |  | 235.9277 |  |  |  |  | 330.5225 |  |  |  |  | 425.5273 |  |  |  |  | 520.8513
VAV
|  |  | FACTORS: | K.l.min | 7 | [17 empty] | FACTORS: | K.l.min | 7 | [17 empty] | FACTORS: | K.l.min | 7
|  |  |  | K.l.max | 21 | [18 empty] | K.l.max | 21 | [18 empty] | K.l.max | 21
|  |  |  | K.dT | 1 | -12 K / dT | [17 empty] | K.dT | 1 | -12 K / dT | [17 empty] | K.dT | 1 | -12 K / dT
|  |  |  | K.H.min(sp) | 1.0037 | Increased draught risk as height increases, Fig 8, Krantz Layout Criteria TB 69 E | [17 empty] | K.H.min(sp) | 1.0037 | Increased draught risk as height increases, Fig 8, Krantz Layout Criteria TB 69 E | [17 empty] | K.H.min(sp) | 1.0037 | Increased draught risk as height increases, Fig 8, Krantz Layout Criteria TB 69 E
|  |  |  | K.H.max(vol) | 1 | Reduce max throw with height to maintain constant volume to prevent stagnation | [17 empty] | K.H.max(vol) | 1 | Reduce max throw with height to maintain constant volume to prevent stagnation | [17 empty] | K.H.max(vol) | 1 | Reduce max throw with height to maintain constant volume to prevent stagnation
|  |  |  | K.2D/3D | 1.1597 | Fig 8 / Fig 7 @ 0.25, Krantz Layout Criteria TB 69 E | [17 empty] | K.2D/3D | 1.1597 | Fig 8 / Fig 7 @ 0.25, Krantz Layout Criteria TB 69 E | [17 empty] | K.2D/3D | 1.1597 | Fig 8 / Fig 7 @ 0.25, Krantz Layout Criteria TB 69 E
|  |  |  | K.adpi | 0.94595 | Adjustment factor for ADPI | [17 empty] | K.adpi | 0.94595 | Adjustment factor for ADPI | [17 empty] | K.adpi | 0.94595 | Adjustment factor for ADPI
|  |  |  | v.room ≤ | 0.23665 | m/s, Krantz Layout Criteria TB 69 E | [17 empty] | v.room ≤ | 0.23665 | m/s, Krantz Layout Criteria TB 69 E | [17 empty] | v.room ≤ | 0.23665 | m/s, Krantz Layout Criteria TB 69 E
|  |  |  | K.h.min | 1.9 | [18 empty] | K.h.min | 1.9 | [18 empty] | K.h.min | 1.9
[25 empty] | INPUT | [19 empty] | INPUT
[24 empty] | H.diffuser = | 2.5 | m | [17 empty] | H.diffuser = | 2.5 | m
|  | PMW- | W.neck | [18 empty] | PMW- | W.neck | dT(cooling) = | -12 | K | [15 empty] | PMW- | W.neck | dT(cooling) = | -12 | K
|  | AD- | mm | [18 empty] | AD- | mm | ADPI ³ | 90 | % | [15 empty] | AD- | mm | ADPI ³ | 90 | %
|  | DN 600 | 577 | [18 empty] | DN 950 | 915 | = | 33.3333 | L/s | [15 empty] | DN 1500 | 1455 | = | 33.3333 | L/s
INPUT
|  |  |  | H.diffuser = | 2.5 | m |  |  |  | m |  |  |  |  | Height to Diffuser Centre-Line = 2.0 to 4.5 m
|  |  |  | dT(cooling) = | -12 | K |  |  |  | K |  |  |  |  | dT = -8 K to -12 K
|  |  |  | ADPI ³ | 90 | % |  |  |  | % |  |  |  |  | 70%, 80%, 90% or 95%
|  |  |  | Turndown to | 100 |  |  |  |  | %
|  |  |  | = | 33.3333 | L/s |  |  |  | L/s
|  |  |  | PMW-AD- | DN600 | [18 empty] | PMW-AD- | DN950 | [18 empty] | PMW-AD- | DN1500
|  |  |  | W.n | 577 | mm | [17 empty] | W.n | 915 | mm | [17 empty] | W.n | 1455 | mm | [14 empty] | mm
|  |  |  | W.f | 612 | mm | [18 empty] | 950 | [19 empty] | 1490 | [15 empty] | mm
|  |  |  | Rows | 1 |  |  |  |  | 2 |  |  |  |  | 3 |  |  |  |  | 4 |  |  |  |  | 1 |  |  |  |  | 2 |  |  |  |  | 3 |  |  |  |  | 4 |  |  |  |  | 1 |  |  |  |  | 2 |  |  |  |  | 3 |  |  |  |  | 4
|  |  |  | H.c | 99 |  |  |  |  | 138 |  |  |  |  | 177 |  |  |  |  | 216 |  |  |  |  | 99 |  |  |  |  | 138 |  |  |  |  | 177 |  |  |  |  | 216 |  |  |  |  | 99 |  |  |  |  | 138 |  |  |  |  | 177 |  |  |  |  | 216 | mm
|  |  |  | H.f | 134 | 35 | 35 | 35 | 35 | 173 | 35 | 35 | 35 | 35 | 212 | 35 | 35 | 35 | 35 | 251 | 35 | 35 | 35 | 35 | 134 | 35 | 35 | 35 | 35 | 173 | 35 | 35 | 35 | 35 | 212 | 35 | 35 | 35 | 35 | 251 | 35 | 35 | 35 | 35 | 134 | 35 | 35 | 35 | 35 | 173 | 35 | 35 | 35 | 35 | 212 | 35 | 35 | 35 | 35 | 251 | mm
|  |  |  | Pt | 3.9158 | Pa |  |  | Pt | 1.9952 | Pa |  |  | Pt | 1.2037 | Pa |  |  | Pt | 0.80345 | Pa |  |  | Pt | 1.5356 | Pa |  |  | Pt | 0.78243 | Pa |  |  | Pt | 0.47205 | Pa |  |  | Pt | 0.31508 | Pa |  |  | Pt | 0.59885 | Pa |  |  | Pt | 0.30512 | Pa |  |  | Pt | 0.18409 | Pa |  |  | Pt | 0.12287 | Pa
|  | H.neck | Throw | Lw | 9.708 | dB(A) | H.neck | Discharge | Lw | <15 | dB(A) | H.neck | Discharge | Lw | <15 | dB(A) | H.neck | Discharge | Lw | <15 | dB(A) | H.neck | Discharge | Lw | <15 | dB(A) | H.neck | Discharge | Lw | <15 | dB(A) | H.neck | Discharge | Lw | <15 | dB(A) | H.neck | Discharge | Lw | <15 | dB(A) | H.neck | Discharge | Lw | <15 | dB(A) | H.neck | Discharge | Lw | <15 | dB(A) | H.neck | Discharge | Lw | <15 | dB(A) | H.neck | Discharge | Lw | <15 | dB(A)
|  | mm | Setting | Lp* | <5 | NC* | mm | Setting | Lp* | <5 | NC* | mm | Setting | Lp* | <5 | NC* | mm | Setting | Lp* | <5 | NC* | mm | Setting | Lp* | <5 | NC* | mm | Setting | Lp* | <5 | NC* | mm | Setting | Lp* | <5 | NC* | mm | Setting | Lp* | <5 | NC* | mm | Setting | Lp* | <5 | NC* | mm | Setting | Lp* | <5 | NC* | mm | Setting | Lp* | <5 | NC* | mm | Setting | Lp* | <5 | NC*
|  |  |  | L Vsp.min | 1.3714 |  |  |  | L Vsp.min | 1.3685 |  |  |  | L Vsp.min | 1.3673 |  |  |  | L Vsp.min | 1.3667 |  |  |  | L Vsp.min | 1.3678 |  |  |  | L Vsp.min | 1.3667 |  |  |  | L Vsp.min | 1.3662 |  |  |  | L Vsp.min | 1.366 |  |  |  | L Vsp.min | 1.3664 |  |  |  | L Vsp.min | 1.366 |  |  |  | L Vsp.min | 1.3658 |  |  |  | L Vsp.min | 1.3657
|  |  |  | L Vsp.max | 2.546 |  |  |  | L Vsp.max | 2.4823 |  |  |  | L Vsp.max | 2.456 |  |  |  | L Vsp.max | 2.4427 |  |  |  | L Vsp.max | 2.467 |  |  |  | L Vsp.max | 2.442 |  |  |  | L Vsp.max | 2.4317 |  |  |  | L Vsp.max | 2.4265 |  |  |  | L Vsp.max | 2.4359 |  |  |  | L Vsp.max | 2.4262 |  |  |  | L Vsp.max | 2.4222 |  |  |  | L Vsp.max | 2.4201
|  |  |  | L throw max | 2.1057 |  |  |  | L throw max | 1.7835 |  |  |  | L throw max | 1.5748 |  |  |  | L throw max | 1.4255 |  |  |  | L throw max | 1.6721 |  |  |  | L throw max | 1.4163 |  |  |  | L throw max | 1.2505 |  |  |  | L throw max | 1.132 |  |  |  | L throw max | 1.326 |  |  |  | L throw max | 1.1231 |  |  |  | L throw max | 0.99169 |  |  |  | L throw max | 0.89771
|  |  |  | W Vsp.min | 2.3761 |  |  |  | W Vsp.min | 2.3712 |  |  |  | W Vsp.min | 2.3691 |  |  |  | W Vsp.min | 2.3681 |  |  |  | W Vsp.min | 2.37 |  |  |  | W Vsp.min | 2.368 |  |  |  | W Vsp.min | 2.3672 |  |  |  | W Vsp.min | 2.3668 |  |  |  | W Vsp.min | 2.3675 |  |  |  | W Vsp.min | 2.3668 |  |  |  | W Vsp.min | 2.3665 |  |  |  | W Vsp.min | 2.3663
|  |  |  | W Vsp.max | 4.4114 |  |  |  | W Vsp.max | 4.301 |  |  |  | W Vsp.max | 4.2555 |  |  |  | W Vsp.max | 4.2325 |  |  |  | W Vsp.max | 4.2746 |  |  |  | W Vsp.max | 4.2312 |  |  |  | W Vsp.max | 4.2134 |  |  |  | W Vsp.max | 4.2044 |  |  |  | W Vsp.max | 4.2207 |  |  |  | W Vsp.max | 4.2038 |  |  |  | W Vsp.max | 4.1968 |  |  |  | W Vsp.max | 4.1933
|  |  |  | W throw max | 3.6484 |  |  |  | W throw max | 3.0902 |  |  |  | W throw max | 2.7286 |  |  |  | W throw max | 2.47 |  |  |  | W throw max | 2.8972 |  |  |  | W throw max | 2.4539 |  |  |  | W throw max | 2.1668 |  |  |  | W throw max | 1.9614 |  |  |  | W throw max | 2.2975 |  |  |  | W throw max | 1.946 |  |  |  | W throw max | 1.7183 |  |  |  | W throw max | 1.5554
|  |  |  | Hmin | 2.1297 | m |  |  | Hmin | 2.1297 | m |  |  | Hmin | 2.1297 | m |  |  | Hmin | 2.1297 | m |  |  | Hmin | 2.0818 | m |  |  | Hmin | 2.0818 | m |  |  | Hmin | 2.0818 | m |  |  | Hmin | 2.0818 | m |  |  | Hmin | 2.0514 | m |  |  | Hmin | 2.0514 | m |  |  | Hmin | 2.0514 | m |  |  | Hmin | 2.0514 | m
|  |  |  | Lmin | 1.3714 | m |  |  | Lmin | 1.3685 | m |  |  | Lmin | 1.3673 | m |  |  | Lmin | 1.3667 | m |  |  | Lmin | 1.3678 | m |  |  | Lmin | 1.3667 | m |  |  | Lmin | 1.3662 | m |  |  | Lmin | 1.366 | m |  |  | Lmin | 1.3664 | m |  |  | Lmin | 1.366 | m |  |  | Lmin | 1.3658 | m |  |  | Lmin | 1.3657 | m
|  |  | S | Lmax | 2.1057 | m |  | S | Lmax | 1.7835 | m |  | S | Lmax | 1.5748 | m |  | S | Lmax | 1.4255 | m |  | S | Lmax | 1.6721 | m |  | S | Lmax | 1.4163 | m |  | S | Lmax | 1.2505 | m |  | S | Lmax | 1.132 | m |  | S | Lmax | 1.326 | m |  | S | Lmax | 1.1231 | m |  | S | Lmax | 0.99169 | m |  | S | Lmax | 0.89771 | m
|  |  | Short | Wmin | 2.3761 | m |  | Short | Wmin | 2.3712 | m |  | Short | Wmin | 2.3691 | m |  | Short | Wmin | 2.3681 | m |  | Short | Wmin | 2.37 | m |  | Short | Wmin | 2.368 | m |  | Short | Wmin | 2.3672 | m |  | Short | Wmin | 2.3668 | m |  | Short | Wmin | 2.3675 | m |  | Short | Wmin | 2.3668 | m |  | Short | Wmin | 2.3665 | m |  | Short | Wmin | 2.3663 | m
|  |  |  | Wmax | 3.6484 | m |  |  | Wmax | 3.0902 | m |  |  | Wmax | 2.7286 | m |  |  | Wmax | 2.47 | m |  |  | Wmax | 2.8972 | m |  |  | Wmax | 2.4539 | m |  |  | Wmax | 2.1668 | m |  |  | Wmax | 1.9614 | m |  |  | Wmax | 2.2975 | m |  |  | Wmax | 1.946 | m |  |  | Wmax | 1.7183 | m |  |  | Wmax | 1.5554 | m
|  |  |  | L,W Vsp.min | 1.8044 |  |  |  | L,W Vsp.min | 1.8006 |  |  |  | L,W Vsp.min | 1.799 |  |  |  | L,W Vsp.min | 1.7983 |  |  |  | L,W Vsp.min | 1.7997 |  |  |  | L,W Vsp.min | 1.7982 |  |  |  | L,W Vsp.min | 1.7976 |  |  |  | L,W Vsp.min | 1.7973 |  |  |  | L,W Vsp.min | 1.7979 |  |  |  | L,W Vsp.min | 1.7973 |  |  |  | L,W Vsp.min | 1.797 |  |  |  | L,W Vsp.min | 1.7969
|  |  |  | L,W Vsp.max | 3.3499 |  |  |  | L,W Vsp.max | 3.2661 |  |  |  | L,W Vsp.max | 3.2315 |  |  |  | L,W Vsp.max | 3.214 |  |  |  | L,W Vsp.max | 3.246 |  |  |  | L,W Vsp.max | 3.2131 |  |  |  | L,W Vsp.max | 3.1995 |  |  |  | L,W Vsp.max | 3.1927 |  |  |  | L,W Vsp.max | 3.2051 |  |  |  | L,W Vsp.max | 3.1922 |  |  |  | L,W Vsp.max | 3.187 |  |  |  | L,W Vsp.max | 3.1843
|  |  |  | L,W throw max | 2.7705 |  |  |  | L,W throw max | 2.3466 |  |  |  | L,W throw max | 2.072 |  |  |  | L,W throw max | 1.8757 |  |  |  | L,W throw max | 2.2001 |  |  |  | L,W throw max | 1.8635 |  |  |  | L,W throw max | 1.6454 |  |  |  | L,W throw max | 1.4895 |  |  |  | L,W throw max | 1.7447 |  |  |  | L,W throw max | 1.4777 |  |  |  | L,W throw max | 1.3048 |  |  |  | L,W throw max | 1.1812
|  |  |  | Lmin | 1.8044 | m |  |  | Lmin | 1.8006 | m |  |  | Lmin | 1.799 | m |  |  | Lmin | 1.7983 | m |  |  | Lmin | 1.7997 | m |  |  | Lmin | 1.7982 | m |  |  | Lmin | 1.7976 | m |  |  | Lmin | 1.7973 | m |  |  | Lmin | 1.7979 | m |  |  | Lmin | 1.7973 | m |  |  | Lmin | 1.797 | m |  |  | Lmin | 1.7969 | m
|  | 99 | M | Lmax | 2.7705 | m | 138 | M | Lmax | 2.3466 | m | 177 | M | Lmax | 2.072 | m | 216 | M | Lmax | 1.8757 | m | 99 | M | Lmax | 2.2001 | m | 138 | M | Lmax | 1.8635 | m | 177 | M | Lmax | 1.6454 | m | 216 | M | Lmax | 1.4895 | m | 99 | M | Lmax | 1.7447 | m | 138 | M | Lmax | 1.4777 | m | 177 | M | Lmax | 1.3048 | m | 216 | M | Lmax | 1.1812 | m
|  | (1-row) | Medium | Wmin | 1.8044 | m | (2-row) | Medium | Wmin | 1.8006 | m | (3-row) | Medium | Wmin | 1.799 | m | (4-row) | Medium | Wmin | 1.7983 | m | (1-row) | Medium | Wmin | 1.7997 | m | (2-row) | Medium | Wmin | 1.7982 | m | (3-row) | Medium | Wmin | 1.7976 | m | (4-row) | Medium | Wmin | 1.7973 | m | (1-row) | Medium | Wmin | 1.7979 | m | (2-row) | Medium | Wmin | 1.7973 | m | (3-row) | Medium | Wmin | 1.797 | m | (4-row) | Medium | Wmin | 1.7969 | m
|  |  |  | Wmax | 2.7705 | m |  |  | Wmax | 2.3466 | m |  |  | Wmax | 2.072 | m |  |  | Wmax | 1.8757 | m |  |  | Wmax | 2.2001 | m |  |  | Wmax | 1.8635 | m |  |  | Wmax | 1.6454 | m |  |  | Wmax | 1.4895 | m |  |  | Wmax | 1.7447 | m |  |  | Wmax | 1.4777 | m |  |  | Wmax | 1.3048 | m |  |  | Wmax | 1.1812 | m
|  |  |  | L Vsp.min | 2.3554 |  |  |  | L Vsp.min | 2.3505 |  |  |  | L Vsp.min | 2.3485 |  |  |  | L Vsp.min | 2.3474 |  |  |  | L Vsp.min | 2.3493 |  |  |  | L Vsp.min | 2.3474 |  |  |  | L Vsp.min | 2.3466 |  |  |  | L Vsp.min | 2.3462 |  |  |  | L Vsp.min | 2.3469 |  |  |  | L Vsp.min | 2.3462 |  |  |  | L Vsp.min | 2.3459 |  |  |  | L Vsp.min | 2.3457
|  |  |  | L Vsp.max | 4.373 |  |  |  | L Vsp.max | 4.2635 |  |  |  | L Vsp.max | 4.2184 |  |  |  | L Vsp.max | 4.1956 |  |  |  | L Vsp.max | 4.2373 |  |  |  | L Vsp.max | 4.1944 |  |  |  | L Vsp.max | 4.1767 |  |  |  | L Vsp.max | 4.1677 |  |  |  | L Vsp.max | 4.1839 |  |  |  | L Vsp.max | 4.1672 |  |  |  | L Vsp.max | 4.1603 |  |  |  | L Vsp.max | 4.1568
|  |  |  | L throw max | 3.6166 |  |  |  | L throw max | 3.0633 |  |  |  | L throw max | 2.7048 |  |  |  | L throw max | 2.4485 |  |  |  | L throw max | 2.872 |  |  |  | L throw max | 2.4326 |  |  |  | L throw max | 2.1479 |  |  |  | L throw max | 1.9444 |  |  |  | L throw max | 2.2775 |  |  |  | L throw max | 1.929 |  |  |  | L throw max | 1.7033 |  |  |  | L throw max | 1.5419
|  |  |  | W Vsp.min | 1.365 |  |  |  | W Vsp.min | 1.3621 |  |  |  | W Vsp.min | 1.361 |  |  |  | W Vsp.min | 1.3604 |  |  |  | W Vsp.min | 1.3615 |  |  |  | W Vsp.min | 1.3603 |  |  |  | W Vsp.min | 1.3599 |  |  |  | W Vsp.min | 1.3596 |  |  |  | W Vsp.min | 1.3601 |  |  |  | W Vsp.min | 1.3596 |  |  |  | W Vsp.min | 1.3594 |  |  |  | W Vsp.min | 1.3593
|  |  |  | W Vsp.max | 2.5342 |  |  |  | W Vsp.max | 2.4707 |  |  |  | W Vsp.max | 2.4446 |  |  |  | W Vsp.max | 2.4314 |  |  |  | W Vsp.max | 2.4556 |  |  |  | W Vsp.max | 2.4307 |  |  |  | W Vsp.max | 2.4204 |  |  |  | W Vsp.max | 2.4152 |  |  |  | W Vsp.max | 2.4246 |  |  |  | W Vsp.max | 2.4149 |  |  |  | W Vsp.max | 2.4109 |  |  |  | W Vsp.max | 2.4089
|  |  |  | W throw max | 2.0959 |  |  |  | W throw max | 1.7752 |  |  |  | W throw max | 1.5675 |  |  |  | W throw max | 1.4189 |  |  |  | W throw max | 1.6643 |  |  |  | W throw max | 1.4097 |  |  |  | W throw max | 1.2447 |  |  |  | W throw max | 1.1268 |  |  |  | W throw max | 1.3198 |  |  |  | W throw max | 1.1179 |  |  |  | W throw max | 0.98708 |  |  |  | W throw max | 0.89354
|  |  |  | Lmin | 2.3554 | m |  |  | Lmin | 2.3505 | m |  |  | Lmin | 2.3485 | m |  |  | Lmin | 2.3474 | m |  |  | Lmin | 2.3493 | m |  |  | Lmin | 2.3474 | m |  |  | Lmin | 2.3466 | m |  |  | Lmin | 2.3462 | m |  |  | Lmin | 2.3469 | m |  |  | Lmin | 2.3462 | m |  |  | Lmin | 2.3459 | m |  |  | Lmin | 2.3457 | m
|  |  | L | Lmax | 3.6166 | m |  | L | Lmax | 3.0633 | m |  | L | Lmax | 2.7048 | m |  | L | Lmax | 2.4485 | m |  | L | Lmax | 2.872 | m |  | L | Lmax | 2.4326 | m |  | L | Lmax | 2.1479 | m |  | L | Lmax | 1.9444 | m |  | L | Lmax | 2.2775 | m |  | L | Lmax | 1.929 | m |  | L | Lmax | 1.7033 | m |  | L | Lmax | 1.5419 | m
|  |  | Long | Wmin | 1.365 | m |  | Long | Wmin | 1.3621 | m |  | Long | Wmin | 1.361 | m |  | Long | Wmin | 1.3604 | m |  | Long | Wmin | 1.3615 | m |  | Long | Wmin | 1.3603 | m |  | Long | Wmin | 1.3599 | m |  | Long | Wmin | 1.3596 | m |  | Long | Wmin | 1.3601 | m |  | Long | Wmin | 1.3596 | m |  | Long | Wmin | 1.3594 | m |  | Long | Wmin | 1.3593 | m
|  |  |  | Wmax | 2.0959 | m |  |  | Wmax | 1.7752 | m |  |  | Wmax | 1.5675 | m |  |  | Wmax | 1.4189 | m |  |  | Wmax | 1.6643 | m |  |  | Wmax | 1.4097 | m |  |  | Wmax | 1.2447 | m |  |  | Wmax | 1.1268 | m |  |  | Wmax | 1.3198 | m |  |  | Wmax | 1.1179 | m |  |  | Wmax | 0.98708 | m |  |  | Wmax | 0.89354 | m
[5 empty] | 1 |  |  |  |  | 2 |  |  |  |  | 3 |  |  |  |  | 4 |  |  |  |  | 5 |  |  |  |  | 6 |  |  |  |  | 7 |  |  |  |  | 8 |  |  |  |  | 9 |  |  |  |  | 10 |  |  |  |  | 11 |  |  |  |  | 12
[5 empty] | 92.2627 |  |  |  |  | 129.2553 |  |  |  |  | 166.4082 |  |  |  |  | 203.6859 |  |  |  |  | 147.3314 |  |  |  |  | 206.4036 |  |  |  |  | 265.7319 |  |  |  |  | 325.2595 |  |  |  |  | 235.9277 |  |  |  |  | 330.5225 |  |  |  |  | 425.5273 |  |  |  |  | 520.8513
RESULTS
|  | Neck Width |  | Wn
|  | Face Width |  | Wf
|  | Rows (Height) |  | Hr
|  | Neck Height |  | Hn
|  | Face Height |  | Hf
|  | Total Pressure |  | Pt
|  | Sound Power Level |  | Lw
|  | Sound Pressure Level |  | Lp*
|  | Min Diffuser Height |  | Hmin | 2.1297 | 0 | 0 | 0 | 0 | 2.1297 | 0 | 0 | 0 | 0 | 2.1297 | 0 | 0 | 0 | 0 | 2.1297 | 0 | 0 | 0 | 0 | 2.0818 | 0 | 0 | 0 | 0 | 2.0818 | 0 | 0 | 0 | 0 | 2.0818 | 0 | 0 | 0 | 0 | 2.0818 | 0 | 0 | 0 | 0 | 2.0514 | 0 | 0 | 0 | 0 | 2.0514 | 0 | 0 | 0 | 0 | 2.0514 | 0 | 0 | 0 | 0 | 2.0514
|  | Short (S) |  | Lmin | 1.3714 | 0 | 0 | 0 | 0 | 1.3685 | 0 | 0 | 0 | 0 | 1.3673 | 0 | 0 | 0 | 0 | 1.3667 | 0 | 0 | 0 | 0 | 1.3678 | 0 | 0 | 0 | 0 | 1.3667 | 0 | 0 | 0 | 0 | 1.3662 | 0 | 0 | 0 | 0 | 1.366 | 0 | 0 | 0 | 0 | 1.3664 | 0 | 0 | 0 | 0 | 1.366 | 0 | 0 | 0 | 0 | 1.3658 | 0 | 0 | 0 | 0 | 1.3657
|  |  |  | Lmax | 2.1057 | 0 | 0 | 0 | 0 | 1.7835 | 0 | 0 | 0 | 0 | 1.5748 | 0 | 0 | 0 | 0 | 1.4255 | 0 | 0 | 0 | 0 | 1.6721 | 0 | 0 | 0 | 0 | 1.4163 | 0 | 0 | 0 | 0 | 1.2505 | 0 | 0 | 0 | 0 | 1.132 | 0 | 0 | 0 | 0 | 1.326 | 0 | 0 | 0 | 0 | 1.1231 | 0 | 0 | 0 | 0 | 0.99169 | 0 | 0 | 0 | 0 | 0.89771
|  |  |  | Bmin | 2.3761 | 0 | 0 | 0 | 0 | 2.3712 | 0 | 0 | 0 | 0 | 2.3691 | 0 | 0 | 0 | 0 | 2.3681 | 0 | 0 | 0 | 0 | 2.37 | 0 | 0 | 0 | 0 | 2.368 | 0 | 0 | 0 | 0 | 2.3672 | 0 | 0 | 0 | 0 | 2.3668 | 0 | 0 | 0 | 0 | 2.3675 | 0 | 0 | 0 | 0 | 2.3668 | 0 | 0 | 0 | 0 | 2.3665 | 0 | 0 | 0 | 0 | 2.3663
|  |  |  | Bmax | 3.6484 | 0 | 0 | 0 | 0 | 3.0902 | 0 | 0 | 0 | 0 | 2.7286 | 0 | 0 | 0 | 0 | 2.47 | 0 | 0 | 0 | 0 | 2.8972 | 0 | 0 | 0 | 0 | 2.4539 | 0 | 0 | 0 | 0 | 2.1668 | 0 | 0 | 0 | 0 | 1.9614 | 0 | 0 | 0 | 0 | 2.2975 | 0 | 0 | 0 | 0 | 1.946 | 0 | 0 | 0 | 0 | 1.7183 | 0 | 0 | 0 | 0 | 1.5554
|  | Medium (M) |  | Lmin | 1.8044 | 0 | 0 | 0 | 0 | 1.8006 | 0 | 0 | 0 | 0 | 1.799 | 0 | 0 | 0 | 0 | 1.7983 | 0 | 0 | 0 | 0 | 1.7997 | 0 | 0 | 0 | 0 | 1.7982 | 0 | 0 | 0 | 0 | 1.7976 | 0 | 0 | 0 | 0 | 1.7973 | 0 | 0 | 0 | 0 | 1.7979 | 0 | 0 | 0 | 0 | 1.7973 | 0 | 0 | 0 | 0 | 1.797 | 0 | 0 | 0 | 0 | 1.7969
|  |  |  | Lmax | 2.7705 | 0 | 138 | 0 | 0 | 2.3466 | 0 | 177 | 0 | 0 | 2.072 | 0 | 216 | 0 | 0 | 1.8757 | 0 | 99 | 0 | 0 | 2.2001 | 0 | 138 | 0 | 0 | 1.8635 | 0 | 177 | 0 | 0 | 1.6454 | 0 | 216 | 0 | 0 | 1.4895 | 0 | 99 | 0 | 0 | 1.7447 | 0 | 138 | 0 | 0 | 1.4777 | 0 | 177 | 0 | 0 | 1.3048 | 0 | 216 | 0 | 0 | 1.1812
|  |  |  | Bmin | 1.8044 | 0 | 0 | 0 | 0 | 1.8006 | 0 | 0 | 0 | 0 | 1.799 | 0 | 0 | 0 | 0 | 1.7983 | 0 | 0 | 0 | 0 | 1.7997 | 0 | 0 | 0 | 0 | 1.7982 | 0 | 0 | 0 | 0 | 1.7976 | 0 | 0 | 0 | 0 | 1.7973 | 0 | 0 | 0 | 0 | 1.7979 | 0 | 0 | 0 | 0 | 1.7973 | 0 | 0 | 0 | 0 | 1.797 | 0 | 0 | 0 | 0 | 1.7969
|  |  |  | Bmax | 2.7705 | 0 | 0 | 0 | 0 | 2.3466 | 0 | 0 | 0 | 0 | 2.072 | 0 | 0 | 0 | 0 | 1.8757 | 0 | 0 | 0 | 0 | 2.2001 | 0 | 0 | 0 | 0 | 1.8635 | 0 | 0 | 0 | 0 | 1.6454 | 0 | 0 | 0 | 0 | 1.4895 | 0 | 0 | 0 | 0 | 1.7447 | 0 | 0 | 0 | 0 | 1.4777 | 0 | 0 | 0 | 0 | 1.3048 | 0 | 0 | 0 | 0 | 1.1812
|  | Long (L) |  | Lmin | 2.3554 | 0 | 0 | 0 | 0 | 2.3505 | 0 | 0 | 0 | 0 | 2.3485 | 0 | 0 | 0 | 0 | 2.3474 | 0 | 0 | 0 | 0 | 2.3493 | 0 | 0 | 0 | 0 | 2.3474 | 0 | 0 | 0 | 0 | 2.3466 | 0 | 0 | 0 | 0 | 2.3462 | 0 | 0 | 0 | 0 | 2.3469 | 0 | 0 | 0 | 0 | 2.3462 | 0 | 0 | 0 | 0 | 2.3459 | 0 | 0 | 0 | 0 | 2.3457
|  |  |  | Lmax | 3.6166 | 0 | 0 | 0 | 0 | 3.0633 | 0 | 0 | 0 | 0 | 2.7048 | 0 | 0 | 0 | 0 | 2.4485 | 0 | 0 | 0 | 0 | 2.872 | 0 | 0 | 0 | 0 | 2.4326 | 0 | 0 | 0 | 0 | 2.1479 | 0 | 0 | 0 | 0 | 1.9444 | 0 | 0 | 0 | 0 | 2.2775 | 0 | 0 | 0 | 0 | 1.929 | 0 | 0 | 0 | 0 | 1.7033 | 0 | 0 | 0 | 0 | 1.5419
|  |  |  | Bmin | 1.365 | 0 | 0 | 0 | 0 | 1.3621 | 0 | 0 | 0 | 0 | 1.361 | 0 | 0 | 0 | 0 | 1.3604 | 0 | 0 | 0 | 0 | 1.3615 | 0 | 0 | 0 | 0 | 1.3603 | 0 | 0 | 0 | 0 | 1.3599 | 0 | 0 | 0 | 0 | 1.3596 | 0 | 0 | 0 | 0 | 1.3601 | 0 | 0 | 0 | 0 | 1.3596 | 0 | 0 | 0 | 0 | 1.3594 | 0 | 0 | 0 | 0 | 1.3593
|  |  |  | Bmax | 2.0959 | 0 | 0 | 0 | 0 | 1.7752 | 0 | 0 | 0 | 0 | 1.5675 | 0 | 0 | 0 | 0 | 1.4189 | 0 | 0 | 0 | 0 | 1.6643 | 0 | 0 | 0 | 0 | 1.4097 | 0 | 0 | 0 | 0 | 1.2447 | 0 | 0 | 0 | 0 | 1.1268 | 0 | 0 | 0 | 0 | 1.3198 | 0 | 0 | 0 | 0 | 1.1179 | 0 | 0 | 0 | 0 | 0.98708 | 0 | 0 | 0 | 0 | 0.89354
|  | Mean Room Air Velocity |  | v
|  | Mean Draught Rating |  | DR
|  | Mean PPD |  | PPD
|  | Satisfies PPD Category |  | (ISO7730)
[16 empty] | 0.30512 | 0.18409 | 0.12287
[16 empty] | <15 | <15 | <15
[16 empty] | <5 | <5 | <5
[11 empty] | 0.30512 | 0.18409 | 0.12287
[11 empty] | <15 | <15 | <15
[11 empty] | <5 | <5 | <5

## PMW-AD Bespoke Calculator
SMARTEMP PRODUCT SELECTION BESPOKE CALCULATOR
Bespoke Perforated Multistream Diffuser [PMW-AD]
Project: | <Project Name>
| Inputs |  |  |  |  | Bespoke Unit Size | [10 empty] | v 3.8 [11/2023]
| Maximum Airflow Rate | 30 | L/s | m3/h | 32.4 - 2160 m³/h |  |  | Number of Columns Wide (Cw) | 2 | 1 ≤ Cw ≤ 21
| VAV Turndown to | 100 | % | 50% to 100%; use 100% for CAV |  |  |  | Number of Rows High (Rh) | 1 | 1 ≤ Rh ≤ 4
| Maximum Total Pressure | 30 | Pa | default 30 Pa |  |  | Size Guide: | Example Widths |  |  |  | Example Heights
[8 empty] | Nominal Size | Wn | Cw |  | Rh | Hf | Hn
| Diffuser Height | 2.5 | m | 2.0 m to 5.5 m (recommended) |  |  |  | DN600 | 577 | 8 |  | 1 | 134 | 99 |  | Cw : number of element columns wide
[8 empty] | DN950 | 915 | 13 |  | 2 | 173 | 138 |  | Rh : number of element rows high
| ΔT (cooling) | -15 | K | 0 K to -15 K (default) |  |  |  | DN1500 | 1455 | 21 |  | 3 | 212 | 177 |  | Wn/Hn : Neck width/height
[12 empty] | 4 | 251 | 216 |  | Wf/Hf : Face width/height
Optional
| ADPI ≥ | 90% |  | default ≥ 90%
Draught Rating & Heating
Auto selection: Average Throw Length and Breadth 26.2 m³/h/m²
| Manual Throw Length | 3.2 | m
| Manual Throw Breadth | 5 | m | = specific airflow rate: 1.9 m³/h/m²
| Specific Airflow Rate | 10 | m³/h/m² | = floor area: 3 m² |  | Thermal Comfort Guide | [8 empty] | example (above): | Cw = 13 elements wide
[6 empty] | ADPI ≥ 95%; ṽ ≤ 0.20 m/s: Premium comfort, sedentary activity, such as in auditoria. | [9 empty] | Rh = 2 elements high
| Room Temperature | 23 | °C |  |  | ADPI ≥ 90%; ṽ ≤ 0.25 m/s: High comfort near-sedentary activity, such as in board rooms, high end offices and libraries. | [9 empty] | Neck: Wn = 915 mm ; Hn = 138 mm
[6 empty] | ADPI ≥ 80%; ṽ ≤ 0.29 m/s: Good comfort near sedentary activity, such as open-plan offices and meeting rooms. | [9 empty] | Face: Wf = 950 mm; Hf = 173 mm
ADPI ≥ 70%; ṽ ≤ 0.33 m/s: Standard comfort medium activity, such as in transient spaces, retail and lobbies.
PMW-AD-Bespoke
Size (n-elements) |  | Cw × Hr |  | 2 × 1
Neck | Width | Wn | [mm] | 172 | Throw Setting Guide | [6 empty] | Key: | Suitable | Not Suitable | Warning
| Height | Hn | [mm] | 99 | [7 empty] | * | Based on 10dB room absorption
Face | Width | Wf | [mm] | 207
| Height | Hf | [mm] | 134
Total Pressure |  | Pt | [Pa] | < 3
Min Recommended Flow Rate |  | Vmin | [m³/h] | 35.1
Sound Power Level |  | Lw | [dB(A)] | < 15
Sound Pressure Level * |  | Lp | [NC] | < 5
Min Recommended Diffuser Height |  | Hmin | [m] | 2.1
Throw Setting | Short (S) | Lmin | [m] | 0.7
|  | Lmax | [m] | 0.9
|  | Bmin | [m] | 1.3
|  | Bmax | [m] | 1.6
| Medium (M) (default) | Lmin | [m] | 0.9
|  | Lmax | [m] | 1.2
|  | Bmin | [m] | 0.9
|  | Bmax | [m] | 1.2
| Long (L) | Lmin | [m] | 1.2
|  | Lmax | [m] | 1.6
|  | Bmin | [m] | 0.7
|  | Bmax | [m] | 0.9
Mean Room Air Velocity |  | v | [m/s] | 0.22
Mean Draught Rating |  | DR | [%] | 24%
Mean PPD |  | PPD | [%] | 11.9%
Satisfies PPD Category (ISO7730) |  |  |  | C
¦PMV¦ (ISO7730 & Ashrae Std 55) |  |  |  | ≤ 0.6
| Throw Setting |  |  |  | short | medium* |  | long
| Discharge Direction (in direction of airflow) |  |  |  | left | centre* |  | right
| Colour |  |  |  | RAL9003* (signal white) |  |  | RAL9005 (jet black) |  |  | other ^
| Accessories |  |  |  | Diffuser Only * | With connection box and VCD (coming late 2020)
| Order Code |  |  | SMARTEMP PMW-AD-BESPOKE-DN172-1-TM-C-RAL9003-0
|  |  |  | click here to see product on smartair.asia | [6 empty] | Copyright © 2017 SMARTAIR DIFFUSION
Group Box 32
Group Box 36
Group Box 26
Group Box 30
Wn
Hn
Cw
Wf
Rh
Hf
Group Box 25
Group Box 41

## PMW_Be_Eqn (hidden)
Inputs
|  |  | L/s | m³/h
|  |  | L/s/m² | m³/h/m² | ²
Airflow Rate Input | 30 | m³/h | [m³/h]
Selection | 2 | m³/h/m² | [m³/h/m²]
Mutiplier | 3.6
Selected Spec Flow | 10
Min Flow | 32.4
Max Flow | 2160
Text | 32.4 - 2160 m³/h
Inputs
Airflow Rate Converted | 8.3333
Turndown % | 1
Turndown Flow rate | 8.3333
Max Total Pressure | 30
Height | 2.5
dT (cooling) | 15 | uses 8K for values between 0 to 8
ADPI | 90%
ADPI-Velocity Chart
95% | 0.2
90% | 0.25
80% | 0.29
70% | 0.33
Target Velocity | 0.25 | m/s
Area Type | 1
Selected L | 3.2
Selected B | 5
Type 2 Selected Area | 16 | Type 2 Spec Flow | 1.9 | m³/h/m²
Converted Spec Flow | 2.7778
Area from spec flow | 3 | m2 | 3
Room Temp | 23
Factors
K.l.min | 7
K.l.max | 21
K.dT | 0.89443 | -12 K / dT
K.H.min(sp) | 1.0037 | Increased draught risk as height increases, Fig 8, Krantz Layout Criteria TB 69 E
K.H.max(vol) | 1 | Reduce max throw with height to maintain constant volume to prevent stagnation
K.2D/3D | 1.1597 | Fig 8 / Fig 7 @ 0.25, Krantz Layout Criteria TB 69 E
v.room ≤ | 0.25 | m/s, Krantz Layout Criteria TB 69 E
K.adpi | 1.0035 | Adjustment factor for ADPI
K.h.min | 1.9
Target Q'' from ADPI
H | Ax | ^B | Q"
2.7 | 2876.0549 | 2.1519 | 145.6158
4 | 2647.6465 | 2.1753 | 129.7716
10 | 2313.9065 | 2.1944 | 110.451
2.5 | 175.9482 | -0.20487 | 145.8334
Q to v conversion
H | Aq | q^b
2.7 | 0.0247 | 0.4647
4 | 0.0267 | 0.4597
10 | 0.0293 | 0.4557
1
|  | Columns (wide) | Cw | 2
|  | Rows (Height) | Hr | 1
|  | Neck Width | Wn | 172.1
|  | Neck Height | Hn | 99.1
|  | Face Width | Wf | 207.1
|  | Face Height | Hf | 134.1
|  | Total Pressure @ | Pt | 2.7308
|  | Min Flow Rate @ -12 | V min | 8.7308
|  | Min Flow Rate @ dT |  | 9.7614
|  | Sound Power Level | Lw | -1.2246
|  | Sound Pressure Level | Lp* | -16.2246
|  | Min Recommended Height | Hmin | 2.091
100% Airflow
|  | L,W Vsp.min |  | 0.94958
|  | L,W Vsp.max |  | 1.5648
|  | L,W throw max |  | 1.2028
|  | Medium (M) | Lmin | 0.94958
|  |  | Lmax | 1.2028
|  |  | Bmin | 0.94958
|  |  | Bmax | 1.2028
|  | L Vsp.min |  | 0.72171
|  | L Vsp.max |  | 1.1893
|  | L throw max |  | 0.91414
|  | W Vsp.min |  | 1.2505
|  | W Vsp.max |  | 2.0606
|  | W throw max |  | 1.5839
|  | Short (S) | Lmin | 0.72171
|  |  | Lmax | 0.91414
|  |  | Bmin | 1.2505
|  |  | Bmax | 1.5839
|  | L Vsp.min |  | 1.2396
|  | L Vsp.max |  | 2.0426
|  | L throw max |  | 1.5701
|  | W Vsp.min |  | 0.71835
|  | W Vsp.max |  | 1.1837
|  | W throw max |  | 0.90988
|  | Long (L) | Lmin | 1.2396
|  |  | Lmax | 1.5701
|  |  | Bmin | 0.71835
|  |  | Bmax | 0.90988
VAV Turndown
|  | Pressure |  | 2.7308
|  | L,W Vsp.min |  | 0.94958
|  | L,W Vsp.max |  | 1.5648
|  | L,W throw max |  | 1.2028
|  | Medium (M) | Lmin | 0.94958
|  |  | Lmax | 1.2028
|  |  | Bmin | 0.94958
|  |  | Bmax | 1.2028
|  | L Vsp.min |  | 0.72171
|  | L Vsp.max |  | 1.1893
|  | L throw max |  | 0.91414
|  | W Vsp.min |  | 1.2505
|  | W Vsp.max |  | 2.0606
|  | W throw max |  | 1.5839
|  | Short (S) | Lmin | 0.72171
|  |  | Lmax | 0.91414
|  |  | Bmin | 1.2505
|  |  | Bmax | 1.5839
|  | L Vsp.min |  | 1.2396
|  | L Vsp.max |  | 2.0426
|  | L throw max |  | 1.5701
|  | W Vsp.min |  | 0.71835
|  | W Vsp.max |  | 1.1837
|  | W throw max |  | 0.90988
|  | Long (L) | Lmin | 1.2396
|  |  | Lmax | 1.5701
|  |  | Bmin | 0.71835
|  |  | Bmax | 0.90988
DISTANCE RESULT
|  | Short (S) | Lmin | 0.7
|  |  | Lmax | 0.9
|  |  | Bmin | 1.3
|  |  | Bmax | 1.6
|  | Medium (M) | Lmin | 0.9
|  |  | Lmax | 1.2
|  |  | Bmin | 0.9
|  |  | Bmax | 1.2
|  | Long (L) | Lmin | 1.2
|  |  | Lmax | 1.6
|  |  | Bmin | 0.7
|  |  | Bmax | 0.9
|  |  | Min Area | 0.91
|  |  | Max Area | 1.44
|  | Short | Avg | 1.175
|  |  | Min Area | 0.81
|  |  | Max Area | 1.44
|  | Medium Avg Area | Avg | 1.125
|  |  | Min Area | 0.84
|  |  | Max Area | 1.44
|  | Long Avg Area | Avg | 1.14
|  | Avg-Avg Area |  | 1.1467
|  | Average Area | 1.1467 | m2 | Numbers for Display
|  | Average area spec flow & format | 7.2674 | L/s/m2 | 26.2
|  | Selected Area | 1.1467 | m2
|  | Selected Spec. Flow | 7.2674 |  | 26.2
|  | Target W | 145.8334 | not used
|  | Q'' Multiplier for v_avg to v_max at 30 Pa) |  | 1.1155
|  | Discharge Velocity - Factor |  | 1.051
|  | W/m2 for selected area |  | 114.5692
|  |  | 2.7 | 0.22364
|  |  | 4 | 0.23608
|  |  | 10 | 0.25421
|  |  | Ax | 0.20496
|  |  | B | 0.094814
|  | Mean Room Air Velocity | 2.5 | 0.22356
|  | Mean Draught Rating | DR | 0.23951
|  | Mean PPD | PPD | 0.11856
|  | Satisfies PPD Category | (ISO7730) | C
|  | PMV |  | 0.59172
|  | Satifies PMV |  | 0.6
|  | SELECTION CRITERIA | TRUE = SHADE
|  | Column shade |  | TRUE
Merged cell shade
|  | Max/Min Pressure |  | TRUE
|  | Min Flow |  | TRUE
|  | Hmin |  | FALSE
|  | Short (S) | Lmin | FALSE
|  |  | Lmax | FALSE
|  |  | Bmin | FALSE
|  |  | Bmax | FALSE
|  | Medium (M) | Lmin | FALSE
|  |  | Lmax | FALSE
|  |  | Bmin | FALSE
|  |  | Bmax | FALSE
|  | Long (L) | Lmin | FALSE
|  |  | Lmax | FALSE
|  |  | Bmin | FALSE
|  |  | Bmax | FALSE
Cell Shading
|  | Short (S) |  | FALSE
FALSE
FALSE
FALSE
|  | Medium (M) |  | FALSE
FALSE
FALSE
FALSE
|  | Long (L) |  | FALSE
FALSE
FALSE
FALSE
SUMMARY
Collated
1
Size |  |  |  | 2 × 1
Neck | Width | Wn | [mm] | 172.1
| Height | Hn | [mm] | 99.1
Face | Width | Wf | [mm] | 207.1
| Height | Hf | [mm] | 134.1
| Total Pressure | Pt | [Pa] | 2.7308
Min Flow |  |  | L/s | 9.7614
| Sound Power Level | Lw | [dB(A)] | -1.2246
| Sound Pressure Level | Lp* | [NC] | -16.2246
| Min Diffuser Height | Hmin | [m] | 2.091
Throw Setting | Short (S) | Lmin | [m] | 0.7
|  | Lmax | [m] | 0.9
|  | Bmin | [m] | 1.3
|  | Bmax | [m] | 1.6
| Medium (M) (default) | Lmin | [m] | 0.9
|  | Lmax | [m] | 1.2
|  | Bmin | [m] | 0.9
|  | Bmax | [m] | 1.2
| Long (L) | Lmin | [m] | 1.2
|  | Lmax | [m] | 1.6
|  | Bmin | [m] | 0.7
|  | Bmax | [m] | 0.9
| Mean Room Air Velocity | v | [m/s] | 0.22356
| Mean Draught Rating | DR | [%] | 0.23951
| Mean PPD | PPD | [%] | 0.11856
| Satisfies PPD Category | (ISO7730) |  | C
Satisfies PMV |  |  |  | 0.6
Numbers Format & units
1
| Rows (Height) | Hr |  | 2 × 1
Neck | Width | Wn | [mm] | 172
| Height | Hn | [mm] | 99
Face | Width | Wf | [mm] | 207
| Height | Hf | [mm] | 134
| Total Pressure | Pt | [Pa] | 2.7
| Min Flowrate |  | m³/h | 35.1
| Sound Power Level | Lw | [dB(A)] | -1.2
| Sound Pressure Level | Lp* | [NC] | -16.2
| Min Diffuser Height | Hmin | [m] | 2.1
Throw Setting | Short (S) | Lmin | [m] | 0.7
|  | Lmax | [m] | 0.9
|  | Bmin | [m] | 1.3
|  | Bmax | [m] | 1.6
| Medium (M) (default) | Lmin | [m] | 0.9
|  | Lmax | [m] | 1.2
|  | Bmin | [m] | 0.9
|  | Bmax | [m] | 1.2
| Long (L) | Lmin | [m] | 1.2
|  | Lmax | [m] | 1.6
|  | Bmin | [m] | 0.7
|  | Bmax | [m] | 0.9
| Mean Room Air Velocity | v | [m/s] | 0.22
| Mean Draught Rating | DR | [%] | 0.24
| Mean PPD | PPD | [%] | 0.119
| Satisfies PPD Category | (ISO7730) |  | C
Satisfies PMV |  |  |  | ≤ 0.6
Results Format
1
| Rows (Height) | Hr |  | 2 × 1
Neck | Width | Wn | [mm] | 172
| Height | Hn | [mm] | 99
Face | Width | Wf | [mm] | 207
| Height | Hf | [mm] | 134
| Total Pressure | Pt | [Pa] | < 3
| Min Flow |  |  | 35.1
| Sound Power Level | Lw | [dB(A)] | < 15
| Sound Pressure Level | Lp* | [NC] | < 5
| Min Diffuser Height | Hmin | [m] | 2.1
Throw Setting | Short (S) | Lmin | [m] | 0.7
|  | Lmax | [m] | 0.9
|  | Bmin | [m] | 1.3
|  | Bmax | [m] | 1.6
| Medium (M) (default) | Lmin | [m] | 0.9
|  | Lmax | [m] | 1.2
|  | Bmin | [m] | 0.9
|  | Bmax | [m] | 1.2
| Long (L) | Lmin | [m] | 1.2
|  | Lmax | [m] | 1.6
|  | Bmin | [m] | 0.7
|  | Bmax | [m] | 0.9
| Mean Room Air Velocity | v | [m/s] | 0.22
| Mean Draught Rating | DR | [%] | 0.24
| Mean PPD | PPD | [%] | 0.119
| Satisfies PPD Category | (ISO7730) |  | C
| PMV |  |  | ≤ 0.6

## PMW-Be-Selection (hidden)
SELECTION
Cw | 2
Hr | 1
Order Size | Check if matches DN size
Cw | DN
8 | 600
13 | 950
21 | 1500
#N/A | 172
Text | DN172-1 | SMARTEMP PMW-AD-BESPOKE
Neck Dimensions | Neck 172 mm × 99 mm
Face Dimensions | Face 207 mm × 134 mm
Throw Setting
Selection | 2
| Code | Description
1 | TS | Short
2 | TM | Medium
3 | TL | Long
Select | TM | Medium
Discharge direction
Discharge select | 2
| Code | Description
1 | L | Left
2 | C | Centre
3 | R | Right
Select | C | Centre
Colour
Colour selection | 1
| Code | Description
1 | RAL9003 | Signal White
2 | RAL9005 | Jet Black
3 | <colour> | custom colour
Select | RAL9003 | Signal White | Signal White (RAL9003)
Accessories
Accessory select | 1
| Code | Description
1 | 0 | Diffuser only (no accessories)
2 | K | With insulated connection box and VCD
Select | 0 | Diffuser only (no accessories)
Description
Bespoke diffuser size DN172 with 1 row(s)
Throw distance set to medium
Centre discharge in direction of airstream
Face painted to Signal White (RAL9003)
| SMARTEMP PMW-AD-BESPOKE- | DN172-1- | TM- | C- | RAL9003- | 0
Order Code: | SMARTEMP PMW-AD-BESPOKE-DN172-1-TM-C-RAL9003-0
Results
Size | 2 × 1
Wn | 172
Hn | 99
Wf | 207
Hf | 134
Pt | < 3
Vmin | 35.1
Lw | < 15
Lp* | < 5
Hmin | 2.1
Lmin | 0.7
Lmax | 0.9
Bmin | 1.3
Bmax | 1.6
Lmin | 0.9
Lmax | 1.2
Bmin | 0.9
Bmax | 1.2
Lmin | 1.2
Lmax | 1.6
Bmin | 0.7
Bmax | 0.9
v | 0.22
DR | 0.24
PPD | 0.119
(ISO7730) | C
PMV | ≤ 0.6
Multiplier | 3.6
Main Page
Airflow | 30 | m³/h | m³/h/m²
TD to | 100%
min flow | 30
dt | -15
height | 2.5
spec flow | 26.2
Airflow Pressure | 30 m³/h @ < 3 Pa total
Min airflow | 30 m³/h (VAV turndown to 100% )
Min Permissible Airflow | 35.1 m³/h @ ΔT = -15 K
Acoustic
SWL | < 15 dB(A)
SPL | < 5 NC (based on 10 dB room absorption)
Comfort for 26.2 m³/h/m²
ADPI | 90%
Mean room air | 0.22 m/s
draught rating | 24% @ room temperature of 23°C
ppd | 11.9%
satisfies category | Category C
PMV | -0.6 ≤ PMV ≤ +0.6 | 0.6
Throw Selection
selectrion | Medium throw selected
selected height | 2.5 m selected install height
height | 2.1 m minimum recommended height
Lmin | 0.9
Lmax | 1.2
Bmin | 0.9
Bmax | 1.2
L | 0.9 m - 1.2 m
B | 0.9 m - 1.2 m

## PMW-AD Bespoke Summary
PMW-AD Performance Calculator Summary
Project | <Project Name>
Company | <Name>
Consultant | <Name>
Product | SMARTEMP PMW-AD Bespoke
Perforated Multistream Adjustable Wall Diffuser
Size | Bespoke diffuser size DN172 with 1 row(s)
Project Summary
Selected Airflow | 30 m³/h @ < 3 Pa total
Min Selected Airflow | 30 m³/h (VAV turndown to 100% )
Min Recommended Airflow | 35.1 m³/h @ ΔT = -15 K
Acoustic Performance
Sound Power Level | < 15 dB(A)
Sound Pressure Level | < 5 NC (based on 10 dB room absorption)
Recommended Layout
Medium throw selected
2.5 m selected install height
Comfort for 26.2 m³/h/m²
ADPI | 90%
Mean Room Air Velocity | 0.22 m/s
Draught Rating (DR) | 24% @ room temperature of 23°C
Mean PPD | 11.9%
Satisfies PPD (ISO7730) | Category C
Satisfies PMV * | -0.6 ≤ PMV ≤ +0.6 | * ISO7730; ASHRAE Std 55
Description | Bespoke diffuser size DN172 with 1 row(s)
Neck 172 mm × 99 mm
Face 207 mm × 134 mm
Throw distance set to medium
Centre discharge in direction of airstream
Face painted to Signal White (RAL9003)
Order Code | SMARTEMP PMW-AD-BESPOKE-DN172-1-TM-C-RAL9003-0
0.9 m - 1.2 m
0.9 m - 1.2 m
2.1 m minimum recommended height

## old Bespoke Calculator (hidden)
Units
Type | 1 |  |  | min | 9 |  | 9 - 600 L/s
Multiplier | 1 |  |  | max | 600
Type | L/s
Type2 | L/s/m²
[5 empty] | FACTORS: |  | K.l.min | 7
[7 empty] | K.l.max | 21
[7 empty] | K.dT | 0.89443 | -12 K / dT
[7 empty] | K.H.min(sp) | 1.0037 | Increased draught risk as height increases, Fig 8, Krantz Layout Criteria TB 69 E
[7 empty] | K.H.max(vol) | 1 | Reduce max throw with height to maintain constant volume to prevent stagnation
[7 empty] | K.2D/3D | 1.1597 | Fig 8 / Fig 7 @ 0.25, Krantz Layout Criteria TB 69 E
[7 empty] | K.adpi | 0.94595 | Adjustment factor for ADPI
[7 empty] | v.room ≤ | 0.23665 | m/s, Krantz Layout Criteria TB 69 E
[7 empty] | K.h.min | 1.9
[8 empty] | INPUT |  |  |  |  | INPUT |  |  |  |  | INPUT
[7 empty] | Elements Long (nL) | [5 empty] | 2 | [6 empty] | 2 <= nL <= 21
[7 empty] | Elements High (nH) | [5 empty] | 1 | [6 empty] | 1 <= nH <= 4
| H.diffuser = | m | 2.5 |  |  |  | H.diffuser = | 2.5 | m |  |  | H.diffuser = | 2.5 | m |  |  | H.diffuser = | 2.5 | m | Height to Diffuser Centre-Line = 2.0 to 4.5 m
| dT(cooling) = | K | -15 |  |  |  | dT(cooling) = | -15 | K | PMW- | W.neck | dT(cooling) = | -15 | K | PMW- | W.neck | dT(cooling) = | -15 | K | dT = -8 K to -12 K
[7 empty] | ADPI ³ | 90 | % | AD- | mm | ADPI ³ | 90 | % | AD- | mm | ADPI ³ | 90 | % | 70%, 80%, 90% or 95%
|  |  | 30 |  |  |  | = | 30 | L/s | DN 950 | 915 | = | 30 | L/s | DN 1500 | 1455 | = | 30 | L/s | 9 L/s to 600 L/s
[8 empty] | PMW-AD- |  |  |  |  | Bespoke
|  | Pt | Pa |  |  |  |  | Pt |  |  |  |  | 36.7871 | [5 empty] | Pa
| Discharge | Lw | dB(A) |  | Length | Height | Throw | Lw |  |  |  |  | 39.7781 | [5 empty] | dB(A)
| Setting | Lp* | NC* |  | mm | mm | Setting | Lp* |  |  |  |  | 24.7781 | [5 empty] | NC*
|  | L Vsp.min | [5 empty] | L Vsp.min |  |  |  |  | 1.5067
|  | L Vsp.max | [5 empty] | L Vsp.max |  |  |  |  | 3.0862
|  | L throw max | [5 empty] | L throw max |  |  |  |  | 3.1021
|  | W Vsp.min | [5 empty] | W Vsp.min |  |  |  |  | 2.6106
|  | W Vsp.max | [5 empty] | W Vsp.max |  |  |  |  | 5.3473
|  | W throw max | [5 empty] | W throw max |  |  |  |  | 5.3749
|  | Hmin | m |  |  |  |  | Hmin |  |  |  |  | 2.3913 | [5 empty] | m
|  | Lmin | m |  |  |  |  | Lmin |  |  |  |  | 1.5067 | [5 empty] | m
| S | Lmax | m |  |  |  | S | Lmax |  |  |  |  | 3.0862 | [5 empty] | m
| Short | Wmin | m |  |  |  | Short | Wmin |  |  |  |  | 2.6106 | [5 empty] | m
|  | Wmax | m |  | L.c | H.c |  | Wmax |  |  |  |  | 5.3473 | [5 empty] | m
|  | L,W Vsp.min | [5 empty] | L,W Vsp.min |  |  |  |  | 1.9824
|  | L,W Vsp.max | [5 empty] | L,W Vsp.max |  |  |  |  | 4.0606
|  | L,W throw max | [5 empty] | L,W throw max |  |  |  |  | 4.0816
|  | Lmin | m |  | 172.1 | 99.1 |  | Lmin |  |  |  |  | 1.9824 | [5 empty] | m
| M | Lmax | m |  |  |  | M | Lmax |  |  |  |  | 4.0606 | [5 empty] | m
| Medium | Wmin | m |  |  |  | Medium | Wmin |  |  |  |  | 1.9824 | [5 empty] | m
|  | Wmax | m |  | L.f | H.f |  | Wmax |  |  |  |  | 4.0606 | [5 empty] | m
|  | L Vsp.min | [5 empty] | L Vsp.min |  |  |  |  | 2.5878
|  | L Vsp.max | [5 empty] | L Vsp.max |  |  |  |  | 5.3007
|  | L throw max | [5 empty] | L throw max |  |  |  |  | 5.3281
|  | W Vsp.min | [5 empty] | W Vsp.min |  |  |  |  | 1.4997
|  | W Vsp.max | [5 empty] | W Vsp.max |  |  |  |  | 3.0718
|  | W throw max | [5 empty] | W throw max |  |  |  |  | 3.0877
|  | Lmin | m |  | 207.1 | 134.1 |  | Lmin |  |  |  |  | 2.5878 | [5 empty] | m
| L | Lmax | m |  |  |  | L | Lmax |  |  |  |  | 5.3007 | [5 empty] | m
| Long | Wmin | m |  |  |  | Long | Wmin |  |  |  |  | 1.4997 | [5 empty] | m
|  | Wmax | m |  |  |  |  | Wmax |  |  |  |  | 3.0718 | [5 empty] | m
[8 empty] | V @Pmax |  |  |  |  | 27.0916
VAV
[5 empty] | FACTORS: |  | K.l.min | 7
[7 empty] | K.l.max | 21
[7 empty] | K.dT | 0.89443 | -12 K / dT
[7 empty] | K.H.min(sp) | 1.0037 | Increased draught risk as height increases, Fig 8, Krantz Layout Criteria TB 69 E
[7 empty] | K.H.max(vol) | 1 | Reduce max throw with height to maintain constant volume to prevent stagnation
[7 empty] | K.2D/3D | 1.1597 | Fig 8 / Fig 7 @ 0.25, Krantz Layout Criteria TB 69 E
[7 empty] | K.adpi | 0.94595 | Adjustment factor for ADPI
[7 empty] | v.room ≤ | 0.23665 | m/s, Krantz Layout Criteria TB 69 E
[7 empty] | K.h.min | 1.9
[8 empty] | INPUT |  |  |  |  | INPUT |  |  |  |  | INPUT
[7 empty] | Elements Long (nL) | [5 empty] | 2 | [6 empty] | 2 <= nL <= 21
[7 empty] | Elements High (nH) | [5 empty] | 1 | [6 empty] | 1 <= nH <= 4
| H.diffuser = | m | 2.5 |  |  |  | H.diffuser = | 2.5 | m |  |  | H.diffuser = | 2.5 | m |  |  | H.diffuser = | 2.5 | m | Height to Diffuser Centre-Line = 2.0 to 4.5 m
| dT(cooling) = | K | -15 |  |  |  | dT(cooling) = | -15 | K | PMW- | W.neck | dT(cooling) = | -15 | K | PMW- | W.neck | dT(cooling) = | -15 | K | dT = -8 K to -12 K
[7 empty] | ADPI ³ | 90 | % | AD- | mm | ADPI ³ | 90 | % | AD- | mm | ADPI ³ | 90 | % | 70%, 80%, 90% or 95%
[7 empty] | Turndown to | [5 empty] | 1
|  |  | 30 |  |  |  | = | 30 | L/s | DN 950 | 915 | = | 30 | L/s | DN 1500 | 1455 | = | 30 | L/s | 9 L/s to 600 L/s
[8 empty] | PMW-AD- |  |  |  |  | Bespoke
|  | Pt | Pa |  |  |  |  | Pt |  |  |  |  | 36.7871 | [5 empty] | Pa
| Discharge | Lw | dB(A) |  | Length | Height | Throw | Lw |  |  |  |  | 39.7781 | [5 empty] | dB(A)
| Setting | Lp* | NC* |  | mm | mm | Setting | Lp* |  |  |  |  | 24.7781 | [5 empty] | NC*
|  | L Vsp.min | [5 empty] | L Vsp.min |  |  |  |  | 1.5067
|  | L Vsp.max | [5 empty] | L Vsp.max |  |  |  |  | 3.0862
|  | L throw max | [5 empty] | L throw max |  |  |  |  | 3.1021
|  | W Vsp.min | [5 empty] | W Vsp.min |  |  |  |  | 2.6106
|  | W Vsp.max | [5 empty] | W Vsp.max |  |  |  |  | 5.3473
|  | W throw max | [5 empty] | W throw max |  |  |  |  | 5.3749
|  | Hmin | m |  |  |  |  | Hmin |  |  |  |  | 2.3913 | [5 empty] | m
|  | Lmin | m |  |  |  |  | Lmin |  |  |  |  | 1.5067 | [5 empty] | m
| S | Lmax | m |  |  |  | S | Lmax |  |  |  |  | 3.0862 | [5 empty] | m
| Short | Wmin | m |  |  |  | Short | Wmin |  |  |  |  | 2.6106 | [5 empty] | m
|  | Wmax | m |  | L.c | H.c |  | Wmax |  |  |  |  | 5.3473 | [5 empty] | m
|  | L,W Vsp.min | [5 empty] | L,W Vsp.min |  |  |  |  | 1.9824
|  | L,W Vsp.max | [5 empty] | L,W Vsp.max |  |  |  |  | 4.0606
|  | L,W throw max | [5 empty] | L,W throw max |  |  |  |  | 4.0816
|  | Lmin | m |  | 172.1 | 99.1 |  | Lmin |  |  |  |  | 1.9824 | [5 empty] | m
| M | Lmax | m |  |  |  | M | Lmax |  |  |  |  | 4.0606 | [5 empty] | m
| Medium | Wmin | m |  |  |  | Medium | Wmin |  |  |  |  | 1.9824 | [5 empty] | m
|  | Wmax | m |  | L.f | H.f |  | Wmax |  |  |  |  | 4.0606 | [5 empty] | m
|  | L Vsp.min | [5 empty] | L Vsp.min |  |  |  |  | 2.5878
|  | L Vsp.max | [5 empty] | L Vsp.max |  |  |  |  | 5.3007
|  | L throw max | [5 empty] | L throw max |  |  |  |  | 5.3281
|  | W Vsp.min | [5 empty] | W Vsp.min |  |  |  |  | 1.4997
|  | W Vsp.max | [5 empty] | W Vsp.max |  |  |  |  | 3.0718
|  | W throw max | [5 empty] | W throw max |  |  |  |  | 3.0877
|  | Lmin | m |  | 207.1 | 134.1 |  | Lmin |  |  |  |  | 2.5878 | [5 empty] | m
| L | Lmax | m |  |  |  | L | Lmax |  |  |  |  | 5.3007 | [5 empty] | m
| Long | Wmin | m |  |  |  | Long | Wmin |  |  |  |  | 1.4997 | [5 empty] | m
|  | Wmax | m |  |  |  |  | Wmax |  |  |  |  | 3.0718 | [5 empty] | m
[8 empty] | V @Pmax |  |  |  |  | 27.0916
Results
| Hmin | 2.3913
| Lmin | 1.5067
| Lmax | 3.0862
| Wmin | 2.6106
| Wmax | 5.3473
| Lmin | 1.9824
| Lmax | 4.0606
| Wmin | 1.9824
| Wmax | 4.0606
| Lmin | 2.5878
| Lmax | 5.3007
| Wmin | 1.4997
| Wmax | 3.0718

## DN 600 (hidden)
| FACTORS: | K.l.min |  | 7
|  | K.l.max |  | 21
|  | K.dT |  | 1 | -12 K / dT
|  | K.H.min(sp) |  | 1.0037 | Increased draught risk as height increases, Fig 8, Krantz Layout Criteria TB 69 E
|  | K.H.max(vol) |  | 1 | Reduce max throw with height to maintain constant volume to prevent stagnation
|  | K.2D/3D |  | 1.1597 | Fig 8 / Fig 7 @ 0.25, Krantz Layout Criteria TB 69 E
|  | K.adpi |  | 0.94595 | Adjustment factor for ADPI
|  | v.room ≤ |  | 0.23665 | m/s, Krantz Layout Criteria TB 69 E
|  | K.h.min |  | 1.9
INPUT
|  |  | H.diffuser = | 2.5 | m | Height to Diffuser Centre-Line = 2.0 to 4.5 m
PMW- | L.neck |  | dT(cooling) = | -12 | K | dT = -8 K to -12 K
AD- | mm | ADPI ≥ 90% | ADPI ³ | 90 | % | 70%, 80%, 90% or 95%
DN 600 | 577 | = |  | 100 | L/s |  | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240 | 250 | 260 | 270
|  | Pt |  | 36.4315 | Pa |  | 30: 3.1618; 40: 5.67; 50: 8.9192; 60: 12.9146; 70: 17.6602; 80: 23.1596; 90: 29.4158; 100: 36.4315; 110: 44.2092; 230: ≤ 20; 240: ≤ 30; 250: ≤ 40; 260: ≤ 50; 270: Pa
H.neck | Throw | Lw |  | 44.8745 | dB(A) |  | 30: <15; 40: 15.5441; 50: 22.6869; 60: 28.523; 70: 33.4574; 80: 37.7317; 90: 41.5019; 100: 44.8745; 110: 47.9254; 230: ≤ 40; 240: ≤ 45; 250: ≤ 50; 260: ≤ 55; 270: dB(A)
mm | Setting | Lp* |  | 29.8745 | NC* |  | 30: <5; 40: <5; 50: 7.6869; 60: 13.523; 70: 18.4574; 80: 22.7317; 90: 26.5019; 100: 29.8745; 110: 32.9254; 230: ≤ 25; 240: ≤ 30; 250: ≤ 35; 260: ≤ 40; 270: NC*
|  | L Vsp.min |  | 2.4595 |  |  | 30: 1.2951; 40: 1.4995; 50: 1.6825; 60: 1.851; 70: 2.0096; 80: 2.161; 90: 2.3074; 100: 2.4503; 110: 2.591
|  | L Vsp.max |  | 6.2792 |  |  | 30: 2.3916; 40: 2.8528; 50: 3.3216; 60: 3.8166; 70: 4.3506; 80: 4.9338; 90: 5.5743; 100: 6.2792; 110: 7.0546
|  | L throw max |  | 6.317 |  |  | 30: 1.8951; 40: 2.5268; 50: 3.1585; 60: 3.7902; 70: 4.4219; 80: 5.0536; 90: 5.6853; 100: 6.317; 110: 6.9487
|  | W Vsp.min |  | 4.2614 |  |  | 30: 2.244; 40: 2.5982; 50: 2.9151; 60: 3.2072; 70: 3.4819; 80: 3.7443; 90: 3.998; 100: 4.2456; 110: 4.4893
|  | W Vsp.max |  | 10.8797 |  |  | 30: 4.1439; 40: 4.943; 50: 5.7553; 60: 6.6129; 70: 7.5382; 80: 8.5487; 90: 9.6584; 100: 10.8797; 110: 12.2233
|  | W throw max |  | 10.9453 |  |  | 30: 3.2836; 40: 4.3781; 50: 5.4727; 60: 6.5672; 70: 7.6617; 80: 8.7563; 90: 9.8508; 100: 10.9453; 110: 12.0399
|  | Hmin |  | 2.389 | m |  | 30: 2.1167; 40: 2.1556; 50: 2.1945; 60: 2.2334; 70: 2.2723; 80: 2.3112; 90: 2.3501; 100: 2.389; 110: 2.4279; 230: * for 10 dB room absorption
|  | Lmin |  | 2.4595 | m |  | 30: 1.2951; 40: 1.4995; 50: 1.6825; 60: 1.851; 70: 2.0096; 80: 2.161; 90: 2.3074; 100: 2.4503; 110: 2.591
| S | Lmax |  | 6.2792 | m |  | 30: 1.8951; 40: 2.5268; 50: 3.1585; 60: 3.7902; 70: 4.3506; 80: 4.9338; 90: 5.5743; 100: 6.2792; 110: 6.9487
| Short | Wmin |  | 4.2614 | m |  | 30: 2.244; 40: 2.5982; 50: 2.9151; 60: 3.2072; 70: 3.4819; 80: 3.7443; 90: 3.998; 100: 4.2456; 110: 4.4893
|  | Wmax |  | 10.8797 | m |  | 30: 3.2836; 40: 4.3781; 50: 5.4727; 60: 6.5672; 70: 7.5382; 80: 8.5487; 90: 9.6584; 100: 10.8797; 110: 12.0399
|  | L,W Vsp.min |  | 3.236 |  |  | 30: 1.704; 40: 1.973; 50: 2.2137; 60: 2.4355; 70: 2.6441; 80: 2.8433; 90: 3.036; 100: 3.224; 110: 3.409
|  | L,W Vsp.max |  | 8.2618 |  |  | 30: 3.1468; 40: 3.7536; 50: 4.3704; 60: 5.0217; 70: 5.7243; 80: 6.4916; 90: 7.3344; 100: 8.2618; 110: 9.2821
|  | L,W throw max |  | 8.3116 |  |  | 30: 2.4935; 40: 3.3246; 50: 4.1558; 60: 4.987; 70: 5.8181; 80: 6.6493; 90: 7.4804; 100: 8.3116; 110: 9.1427
|  | Lmin |  | 3.236 | m |  | 30: 1.704; 40: 1.973; 50: 2.2137; 60: 2.4355; 70: 2.6441; 80: 2.8433; 90: 3.036; 100: 3.224; 110: 3.409; 190: `
99 | M | Lmax |  | 8.2618 | m |  | 30: 2.4935; 40: 3.3246; 50: 4.1558; 60: 4.987; 70: 5.7243; 80: 6.4916; 90: 7.3344; 100: 8.2618; 110: 9.1427
(1-row) | Medium | Wmin |  | 3.236 | m |  | 30: 1.704; 40: 1.973; 50: 2.2137; 60: 2.4355; 70: 2.6441; 80: 2.8433; 90: 3.036; 100: 3.224; 110: 3.409
|  | Wmax |  | 8.2618 | m |  | 30: 2.4935; 40: 3.3246; 50: 4.1558; 60: 4.987; 70: 5.7243; 80: 6.4916; 90: 7.3344; 100: 8.2618; 110: 9.1427
|  | L Vsp.min |  | 4.2243 |  |  | 30: 2.2244; 40: 2.5756; 50: 2.8897; 60: 3.1793; 70: 3.4516; 80: 3.7117; 90: 3.9631; 100: 4.2086; 110: 4.4502
|  | L Vsp.max |  | 10.7849 |  |  | 30: 4.1078; 40: 4.8999; 50: 5.7052; 60: 6.5553; 70: 7.4726; 80: 8.4742; 90: 9.5743; 100: 10.7849; 110: 12.1168
|  | L throw max |  | 10.8499 |  |  | 30: 3.255; 40: 4.34; 50: 5.425; 60: 6.51; 70: 7.595; 80: 8.68; 90: 9.765; 100: 10.8499; 110: 11.9349
|  | W Vsp.min |  | 2.448 |  |  | 30: 1.2891; 40: 1.4926; 50: 1.6746; 60: 1.8424; 70: 2.0002; 80: 2.151; 90: 2.2967; 100: 2.4389; 110: 2.5789
|  | W Vsp.max |  | 6.25 |  |  | 30: 2.3805; 40: 2.8395; 50: 3.3062; 60: 3.7988; 70: 4.3304; 80: 4.9109; 90: 5.5484; 100: 6.25; 110: 7.0218
|  | W throw max |  | 6.2876 |  |  | 30: 1.8863; 40: 2.5151; 50: 3.1438; 60: 3.7726; 70: 4.4013; 80: 5.0301; 90: 5.6589; 100: 6.2876; 110: 6.9164
|  | Lmin |  | 4.2243 | m |  | 30: 2.2244; 40: 2.5756; 50: 2.8897; 60: 3.1793; 70: 3.4516; 80: 3.7117; 90: 3.9631; 100: 4.2086; 110: 4.4502
| L | Lmax |  | 10.7849 | m |  | 30: 3.255; 40: 4.34; 50: 5.425; 60: 6.51; 70: 7.4726; 80: 8.4742; 90: 9.5743; 100: 10.7849; 110: 11.9349
| Long | Wmin |  | 2.448 | m |  | 30: 1.2891; 40: 1.4926; 50: 1.6746; 60: 1.8424; 70: 2.0002; 80: 2.151; 90: 2.2967; 100: 2.4389; 110: 2.5789
|  | Wmax |  | 6.25 | m |  | 30: 1.8863; 40: 2.5151; 50: 3.1438; 60: 3.7726; 70: 4.3304; 80: 4.9109; 90: 5.5484; 100: 6.25; 110: 6.9164
|  | Pt |  | 18.5624 | Pa |  | 50: 4.5445; 60: 6.5802; 70: 8.9981; 80: 11.8001; 90: 14.9878; 100: 18.5624; 110: 22.5252; 120: 26.8774; 130: 31.62; 140: 36.7538; 150: 42.2799; 160: 48.199; 170: 54.5119
H.neck | Throw | Lw |  | 35.6854 | dB(A) |  | 50: <15; 60: 19.3338; 70: 24.2682; 80: 28.5425; 90: 32.3128; 100: 35.6854; 110: 38.7363; 120: 41.5215; 130: 44.0837; 140: 46.4558; 150: 48.6643; 160: 50.7302; 170: 52.6708
mm | Setting | Lp* |  | 20.6854 | NC* |  | 50: <5; 60: <5; 70: 9.2682; 80: 13.5425; 90: 17.3128; 100: 20.6854; 110: 23.7363; 120: 26.5215; 130: 29.0837; 140: 31.4558; 150: 33.6643; 160: 35.7302; 170: 37.6708
|  | L Vsp.min |  | 2.4132 |  |  | 50: 1.6745; 60: 1.8384; 70: 1.9909; 80: 2.1348; 90: 2.2721; 100: 2.4042; 110: 2.5323; 120: 2.6572; 130: 2.7796; 140: 2.9002; 150: 3.0195; 160: 3.1378; 170: 3.2556
|  | L Vsp.max |  | 5.2519 |  |  | 50: 3.1438; 60: 3.5345; 70: 3.934; 80: 4.3497; 90: 4.7874; 100: 5.2519; 110: 5.7472; 120: 6.2768; 130: 6.844; 140: 7.4515; 150: 8.1021; 160: 8.7983; 170: 9.5423
|  | L throw max |  | 5.3504 |  |  | 50: 2.6752; 60: 3.2103; 70: 3.7453; 80: 4.2804; 90: 4.8154; 100: 5.3504; 110: 5.8855; 120: 6.4205; 130: 6.9556; 140: 7.1895; 150: 7.1895; 160: 7.1895; 170: 7.1895
|  | W Vsp.min |  | 4.1813 |  |  | 50: 2.9013; 60: 3.1853; 70: 3.4495; 80: 3.6989; 90: 3.9368; 100: 4.1657; 110: 4.3876; 120: 4.604; 130: 4.8162; 140: 5.0252; 150: 5.2318; 160: 5.4368; 170: 5.6409
|  | W Vsp.max |  | 9.0998 |  |  | 50: 5.4472; 60: 6.1241; 70: 6.8163; 80: 7.5366; 90: 8.295; 100: 9.0998; 110: 9.9579; 120: 10.8756; 130: 11.8583; 140: 12.9111; 150: 14.0384; 160: 15.2446; 170: 16.5336
|  | W throw max |  | 9.2706 |  |  | 50: 4.6353; 60: 5.5623; 70: 6.4894; 80: 7.4165; 90: 8.3435; 100: 9.2706; 110: 10.1976; 120: 11.1247; 130: 12.0517; 140: 12.457; 150: 12.457; 160: 12.457; 170: 12.457
|  | Hmin |  | 2.389 | m |  | 50: 2.1945; 60: 2.2334; 70: 2.2723; 80: 2.3112; 90: 2.3501; 100: 2.389; 110: 2.4279; 120: 2.4668; 130: 2.5057; 140: 2.5446; 150: 2.5835; 160: 2.6224; 170: 2.6613
|  | Lmin |  | 2.4132 | m |  | 50: 1.6745; 60: 1.8384; 70: 1.9909; 80: 2.1348; 90: 2.2721; 100: 2.4042; 110: 2.5323; 120: 2.6572; 130: 2.7796; 140: 2.9002; 150: 3.0195; 160: 3.1378; 170: 3.2556
| S | Lmax |  | 5.2519 | m |  | 50: 2.6752; 60: 3.2103; 70: 3.7453; 80: 4.2804; 90: 4.7874; 100: 5.2519; 110: 5.7472; 120: 6.2768; 130: 6.844; 140: 7.1895; 150: 7.1895; 160: 7.1895; 170: 7.1895
| Short | Wmin |  | 4.1813 | m |  | 50: 2.9013; 60: 3.1853; 70: 3.4495; 80: 3.6989; 90: 3.9368; 100: 4.1657; 110: 4.3876; 120: 4.604; 130: 4.8162; 140: 5.0252; 150: 5.2318; 160: 5.4368; 170: 5.6409
|  | Wmax |  | 9.0998 | m |  | 50: 4.6353; 60: 5.5623; 70: 6.4894; 80: 7.4165; 90: 8.295; 100: 9.0998; 110: 9.9579; 120: 10.8756; 130: 11.8583; 140: 12.457; 150: 12.457; 160: 12.457; 170: 12.457
|  | L,W Vsp.min |  | 3.1752 |  |  | 50: 2.2032; 60: 2.4188; 70: 2.6195; 80: 2.8089; 90: 2.9895; 100: 3.1634; 110: 3.3319; 120: 3.4962; 130: 3.6573; 140: 3.816; 150: 3.9729; 160: 4.1286; 170: 4.2836
|  | L,W Vsp.max |  | 6.9101 |  |  | 50: 4.1364; 60: 4.6505; 70: 5.1762; 80: 5.7231; 90: 6.299; 100: 6.9101; 110: 7.5618; 120: 8.2587; 130: 9.0049; 140: 9.8043; 150: 10.6604; 160: 11.5763; 170: 12.5552
|  | L,W throw max |  | 7.0398 |  |  | 50: 3.5199; 60: 4.2239; 70: 4.9279; 80: 5.6319; 90: 6.3358; 100: 7.0398; 110: 7.7438; 120: 8.4478; 130: 9.1518; 140: 9.4595; 150: 9.4595; 160: 9.4595; 170: 9.4595
|  | Lmin |  | 3.1752 | m |  | 50: 2.2032; 60: 2.4188; 70: 2.6195; 80: 2.8089; 90: 2.9895; 100: 3.1634; 110: 3.3319; 120: 3.4962; 130: 3.6573; 140: 3.816; 150: 3.9729; 160: 4.1286; 170: 4.2836
138 | M | Lmax |  | 6.9101 | m |  | 50: 3.5199; 60: 4.2239; 70: 4.9279; 80: 5.6319; 90: 6.299; 100: 6.9101; 110: 7.5618; 120: 8.2587; 130: 9.0049; 140: 9.4595; 150: 9.4595; 160: 9.4595; 170: 9.4595
(2-row) | Medium | Wmin |  | 3.1752 | m |  | 50: 2.2032; 60: 2.4188; 70: 2.6195; 80: 2.8089; 90: 2.9895; 100: 3.1634; 110: 3.3319; 120: 3.4962; 130: 3.6573; 140: 3.816; 150: 3.9729; 160: 4.1286; 170: 4.2836
|  | Wmax |  | 6.9101 | m |  | 50: 3.5199; 60: 4.2239; 70: 4.9279; 80: 5.6319; 90: 6.299; 100: 6.9101; 110: 7.5618; 120: 8.2587; 130: 9.0049; 140: 9.4595; 150: 9.4595; 160: 9.4595; 170: 9.4595
|  | L Vsp.min |  | 4.1449 |  |  | 50: 2.876; 60: 3.1575; 70: 3.4195; 80: 3.6667; 90: 3.9025; 100: 4.1294; 110: 4.3494; 120: 4.5639; 130: 4.7742; 140: 4.9814; 150: 5.1862; 160: 5.3895; 170: 5.5918
|  | L Vsp.max |  | 9.0205 |  |  | 50: 5.3997; 60: 6.0708; 70: 6.7569; 80: 7.4709; 90: 8.2227; 100: 9.0205; 110: 9.8712; 120: 10.7809; 130: 11.755; 140: 12.7985; 150: 13.916; 160: 15.1117; 170: 16.3895
|  | L throw max |  | 9.1898 |  |  | 50: 4.5949; 60: 5.5139; 70: 6.4329; 80: 7.3518; 90: 8.2708; 100: 9.1898; 110: 10.1088; 120: 11.0278; 130: 11.9467; 140: 12.3485; 150: 12.3485; 160: 12.3485; 170: 12.3485
|  | W Vsp.min |  | 2.402 |  |  | 50: 1.6667; 60: 1.8298; 70: 1.9816; 80: 2.1249; 90: 2.2615; 100: 2.393; 110: 2.5205; 120: 2.6448; 130: 2.7667; 140: 2.8867; 150: 3.0054; 160: 3.1232; 170: 3.2405
|  | W Vsp.max |  | 5.2274 |  |  | 50: 3.1292; 60: 3.5181; 70: 3.9157; 80: 4.3295; 90: 4.7651; 100: 5.2274; 110: 5.7204; 120: 6.2476; 130: 6.8121; 140: 7.4169; 150: 8.0645; 160: 8.7574; 170: 9.4979
|  | W throw max |  | 5.3256 |  |  | 50: 2.6628; 60: 3.1953; 70: 3.7279; 80: 4.2604; 90: 4.793; 100: 5.3256; 110: 5.8581; 120: 6.3907; 130: 6.9232; 140: 7.1561; 150: 7.1561; 160: 7.1561; 170: 7.1561
|  | Lmin |  | 4.1449 | m |  | 50: 2.876; 60: 3.1575; 70: 3.4195; 80: 3.6667; 90: 3.9025; 100: 4.1294; 110: 4.3494; 120: 4.5639; 130: 4.7742; 140: 4.9814; 150: 5.1862; 160: 5.3895; 170: 5.5918
| L | Lmax |  | 9.0205 | m |  | 50: 4.5949; 60: 5.5139; 70: 6.4329; 80: 7.3518; 90: 8.2227; 100: 9.0205; 110: 9.8712; 120: 10.7809; 130: 11.755; 140: 12.3485; 150: 12.3485; 160: 12.3485; 170: 12.3485
| Long | Wmin |  | 2.402 | m |  | 50: 1.6667; 60: 1.8298; 70: 1.9816; 80: 2.1249; 90: 2.2615; 100: 2.393; 110: 2.5205; 120: 2.6448; 130: 2.7667; 140: 2.8867; 150: 3.0054; 160: 3.1232; 170: 3.2405
|  | Wmax |  | 5.2274 | m |  | 50: 2.6628; 60: 3.1953; 70: 3.7279; 80: 4.2604; 90: 4.7651; 100: 5.2274; 110: 5.7204; 120: 6.2476; 130: 6.8121; 140: 7.1561; 150: 7.1561; 160: 7.1561; 170: 7.1561
|  | Pt |  | 11.199 | Pa |  |  |  |  | 3.9699 | 5.4287 | 7.1192 | 9.0424 | 11.199 | 13.5899 | 16.2157 | 19.0769 | 22.1743 | 25.5083 | 29.0794 | 32.8881 | 36.9347 | 41.2199 | 45.7438 | 50.5069 | 55.5095
H.neck | Throw | Lw |  | 28.7992 | dB(A) |  |  |  |  | <15 | 17.382 | 21.6563 | 25.4266 | 28.7992 | 31.85 | 34.6353 | 37.1974 | 39.5696 | 41.7781 | 43.844 | 45.7846 | 47.6142 | 49.3449 | 50.9868 | 52.5486 | 54.0377
mm | Setting | Lp* |  | 13.7992 | NC* |  |  |  |  | <5 | <5 | 6.6563 | 10.4266 | 13.7992 | 16.85 | 19.6353 | 22.1974 | 24.5696 | 26.7781 | 28.844 | 30.7846 | 32.6142 | 34.3449 | 35.9868 | 37.5486 | 39.0377
|  | L Vsp.min |  | 2.3941 | [5 empty] | 1.8332 | 1.9832 | 2.124 | 2.2576 | 2.3852 | 2.5081 | 2.6271 | 2.7428 | 2.8557 | 2.9665 | 3.0754 | 3.1829 | 3.2892 | 3.3946 | 3.4992 | 3.6035 | 3.7074
|  | L Vsp.max |  | 4.8286 | [5 empty] | 3.4183 | 3.7623 | 4.109 | 4.4632 | 4.8286 | 5.2084 | 5.6054 | 6.0218 | 6.4598 | 6.9213 | 7.4079 | 7.9214 | 8.4632 | 9.0347 | 9.6372 | 10.272 | 10.9403
|  | L throw max |  | 4.7244 | [5 empty] | 2.8346 | 3.3071 | 3.7795 | 4.2519 | 4.7244 | 5.1968 | 5.6692 | 6.1417 | 6.6141 | 7.0865 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895
|  | W Vsp.min |  | 4.1483 | [5 empty] | 3.1763 | 3.4362 | 3.6802 | 3.9116 | 4.1328 | 4.3458 | 4.5519 | 4.7523 | 4.9481 | 5.14 | 5.3287 | 5.5149 | 5.6991 | 5.8817 | 6.063 | 6.2436 | 6.4237
|  | W Vsp.max |  | 8.3663 | [5 empty] | 5.9227 | 6.5189 | 7.1196 | 7.7332 | 8.3663 | 9.0245 | 9.7122 | 10.4338 | 11.1927 | 11.9923 | 12.8355 | 13.7252 | 14.6639 | 15.6541 | 16.6981 | 17.798 | 18.9559
|  | W throw max |  | 8.1858 | [5 empty] | 4.9115 | 5.73 | 6.5486 | 7.3672 | 8.1858 | 9.0043 | 9.8229 | 10.6415 | 11.4601 | 12.2787 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457
|  | Hmin |  | 2.389 | m |  |  |  |  | 2.2334 | 2.2723 | 2.3112 | 2.3501 | 2.389 | 2.4279 | 2.4668 | 2.5057 | 2.5446 | 2.5835 | 2.6224 | 2.6613 | 2.7002 | 2.7391 | 2.778 | 2.8169 | 2.8558
|  | Lmin |  | 2.3941 | m |  |  |  |  | 1.8332 | 1.9832 | 2.124 | 2.2576 | 2.3852 | 2.5081 | 2.6271 | 2.7428 | 2.8557 | 2.9665 | 3.0754 | 3.1829 | 3.2892 | 3.3946 | 3.4992 | 3.6035 | 3.7074
| S | Lmax |  | 4.7244 | m |  |  |  |  | 2.8346 | 3.3071 | 3.7795 | 4.2519 | 4.7244 | 5.1968 | 5.6054 | 6.0218 | 6.4598 | 6.9213 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895
| Short | Wmin |  | 4.1483 | m |  |  |  |  | 3.1763 | 3.4362 | 3.6802 | 3.9116 | 4.1328 | 4.3458 | 4.5519 | 4.7523 | 4.9481 | 5.14 | 5.3287 | 5.5149 | 5.6991 | 5.8817 | 6.063 | 6.2436 | 6.4237
|  | Wmax |  | 8.1858 | m |  |  |  |  | 4.9115 | 5.73 | 6.5486 | 7.3672 | 8.1858 | 9.0043 | 9.7122 | 10.4338 | 11.1927 | 11.9923 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457
|  | L,W Vsp.min |  | 3.1501 | [5 empty] | 2.412 | 2.6094 | 2.7947 | 2.9704 | 3.1384 | 3.3001 | 3.4566 | 3.6088 | 3.7574 | 3.9032 | 4.0465 | 4.1879 | 4.3277 | 4.4664 | 4.6041 | 4.7412 | 4.878
|  | L,W Vsp.max |  | 6.3532 | [5 empty] | 4.4976 | 4.9503 | 5.4064 | 5.8724 | 6.3532 | 6.8529 | 7.3752 | 7.9231 | 8.4994 | 9.1066 | 9.747 | 10.4226 | 11.1354 | 11.8873 | 12.6801 | 13.5153 | 14.3946
|  | L,W throw max |  | 6.2161 | [5 empty] | 3.7296 | 4.3512 | 4.9728 | 5.5945 | 6.2161 | 6.8377 | 7.4593 | 8.0809 | 8.7025 | 9.3241 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595
|  | Lmin |  | 3.1501 | m |  |  |  |  | 2.412 | 2.6094 | 2.7947 | 2.9704 | 3.1384 | 3.3001 | 3.4566 | 3.6088 | 3.7574 | 3.9032 | 4.0465 | 4.1879 | 4.3277 | 4.4664 | 4.6041 | 4.7412 | 4.878
177 | M | Lmax |  | 6.2161 | m |  |  |  |  | 3.7296 | 4.3512 | 4.9728 | 5.5945 | 6.2161 | 6.8377 | 7.3752 | 7.9231 | 8.4994 | 9.1066 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595
(3-row) | Medium | Wmin |  | 3.1501 | m |  |  |  |  | 2.412 | 2.6094 | 2.7947 | 2.9704 | 3.1384 | 3.3001 | 3.4566 | 3.6088 | 3.7574 | 3.9032 | 4.0465 | 4.1879 | 4.3277 | 4.4664 | 4.6041 | 4.7412 | 4.878
|  | Wmax |  | 6.2161 | m |  |  |  |  | 3.7296 | 4.3512 | 4.9728 | 5.5945 | 6.2161 | 6.8377 | 7.3752 | 7.9231 | 8.4994 | 9.1066 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595
|  | L Vsp.min |  | 4.1121 | [5 empty] | 3.1486 | 3.4063 | 3.6481 | 3.8775 | 4.0968 | 4.3079 | 4.5122 | 4.7109 | 4.905 | 5.0952 | 5.2823 | 5.4669 | 5.6494 | 5.8304 | 6.0102 | 6.1892 | 6.3677
|  | L Vsp.max |  | 8.2934 | [5 empty] | 5.8711 | 6.4621 | 7.0575 | 7.6658 | 8.2934 | 8.9458 | 9.6276 | 10.3429 | 11.0952 | 11.8878 | 12.7237 | 13.6056 | 14.5362 | 15.5177 | 16.5526 | 17.6429 | 18.7907
|  | L throw max |  | 8.1144 | [5 empty] | 4.8687 | 5.6801 | 6.4916 | 7.303 | 8.1144 | 8.9259 | 9.7373 | 10.5488 | 11.3602 | 12.1717 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485
|  | W Vsp.min |  | 2.383 | [5 empty] | 1.8246 | 1.974 | 2.1141 | 2.2471 | 2.3741 | 2.4965 | 2.6148 | 2.73 | 2.8425 | 2.9527 | 3.0611 | 3.1681 | 3.2739 | 3.3788 | 3.483 | 3.5867 | 3.6902
|  | W Vsp.max |  | 4.8061 | [5 empty] | 3.4024 | 3.7448 | 4.0899 | 4.4424 | 4.8061 | 5.1842 | 5.5793 | 5.9938 | 6.4297 | 6.8891 | 7.3735 | 7.8846 | 8.4238 | 8.9926 | 9.5923 | 10.2242 | 10.8894
|  | W throw max |  | 4.7024 | [5 empty] | 2.8214 | 3.2917 | 3.7619 | 4.2321 | 4.7024 | 5.1726 | 5.6429 | 6.1131 | 6.5833 | 7.0536 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561
|  | Lmin |  | 4.1121 | m |  |  |  |  | 3.1486 | 3.4063 | 3.6481 | 3.8775 | 4.0968 | 4.3079 | 4.5122 | 4.7109 | 4.905 | 5.0952 | 5.2823 | 5.4669 | 5.6494 | 5.8304 | 6.0102 | 6.1892 | 6.3677
| L | Lmax |  | 8.1144 | m |  |  |  |  | 4.8687 | 5.6801 | 6.4916 | 7.303 | 8.1144 | 8.9259 | 9.6276 | 10.3429 | 11.0952 | 11.8878 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485
| Long | Wmin |  | 2.383 | m |  |  |  |  | 1.8246 | 1.974 | 2.1141 | 2.2471 | 2.3741 | 2.4965 | 2.6148 | 2.73 | 2.8425 | 2.9527 | 3.0611 | 3.1681 | 3.2739 | 3.3788 | 3.483 | 3.5867 | 3.6902
|  | Wmax |  | 4.7024 | m |  |  |  |  | 2.8214 | 3.2917 | 3.7619 | 4.2321 | 4.7024 | 5.1726 | 5.5793 | 5.9938 | 6.4297 | 6.8891 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561
|  | Pt |  | 7.4749 | Pa | [5 empty] | 3.6235 | 4.7518 | 6.0355 | 7.4749 | 9.0708 | 10.8234 | 12.7332 | 14.8005 | 17.0258 | 19.4094 | 21.9516 | 24.6526 | 27.5127 | 30.5323 | 33.7115 | 37.0506 | 40.5497 | 44.2092 | 48.0293 | 52.01 | 56.1517
H.neck | Throw | Lw |  | 23.2898 | dB(A) | [5 empty] | <15 | 16.147 | 19.9173 | 23.2898 | 26.3407 | 29.126 | 31.6881 | 34.0603 | 36.2688 | 38.3347 | 40.2753 | 42.1049 | 43.8356 | 45.4775 | 47.0393 | 48.5284 | 49.9513 | 51.3136 | 52.6203 | 53.8758 | 55.0838
mm | Setting | Lp* |  | 8.2898 | NC* | [5 empty] | <5 | <5 | <5 | 8.2898 | 11.3407 | 14.126 | 16.6881 | 19.0603 | 21.2688 | 23.3347 | 25.2753 | 27.1049 | 28.8356 | 30.4775 | 32.0393 | 33.5284 | 34.9513 | 36.3136 | 37.6203 | 38.8758 | 40.0838
|  | L Vsp.min |  | 2.3845 | [6 empty] | 1.9793 | 2.1185 | 2.2502 | 2.3756 | 2.4959 | 2.6118 | 2.7241 | 2.8332 | 2.9397 | 3.0439 | 3.1461 | 3.2467 | 3.3458 | 3.4438 | 3.5407 | 3.6368 | 3.7322 | 3.8271 | 3.9216 | 4.0158 | 4.1099
|  | L Vsp.max |  | 4.6145 | [6 empty] | 3.6755 | 3.9873 | 4.2992 | 4.6145 | 4.9359 | 5.2658 | 5.606 | 5.9582 | 6.324 | 6.7048 | 7.1016 | 7.5159 | 7.9485 | 8.4004 | 8.8728 | 9.3663 | 9.8819 | 10.4203 | 10.9824 | 11.5689 | 12.1806
|  | L throw max |  | 4.2766 | [6 empty] | 2.9936 | 3.4213 | 3.849 | 4.2766 | 4.7043 | 5.132 | 5.5596 | 5.9873 | 6.415 | 6.8426 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895
|  | W Vsp.min |  | 4.1316 | [6 empty] | 3.4295 | 3.6707 | 3.8989 | 4.1162 | 4.3246 | 4.5255 | 4.72 | 4.9091 | 5.0936 | 5.2741 | 5.4512 | 5.6254 | 5.7972 | 5.9669 | 6.1348 | 6.3013 | 6.4667 | 6.6311 | 6.7948 | 6.9581 | 7.121
|  | W Vsp.max |  | 7.9954 | [6 empty] | 6.3684 | 6.9087 | 7.449 | 7.9954 | 8.5523 | 9.1239 | 9.7133 | 10.3236 | 10.9575 | 11.6171 | 12.3048 | 13.0225 | 13.7721 | 14.5552 | 15.3736 | 16.2287 | 17.122 | 18.055 | 19.029 | 20.0452 | 21.1049
|  | W throw max |  | 7.41 | [6 empty] | 5.187 | 5.928 | 6.669 | 7.41 | 8.151 | 8.892 | 9.633 | 10.374 | 11.115 | 11.856 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457
|  | Hmin |  | 2.389 | m | [5 empty] | 2.2723 | 2.3112 | 2.3501 | 2.389 | 2.4279 | 2.4668 | 2.5057 | 2.5446 | 2.5835 | 2.6224 | 2.6613 | 2.7002 | 2.7391 | 2.778 | 2.8169 | 2.8558 | 2.8947 | 2.9336 | 2.9725 | 3.0114 | 3.0503
|  | Lmin |  | 2.3845 | m | [5 empty] | 1.9793 | 2.1185 | 2.2502 | 2.3756 | 2.4959 | 2.6118 | 2.7241 | 2.8332 | 2.9397 | 3.0439 | 3.1461 | 3.2467 | 3.3458 | 3.4438 | 3.5407 | 3.6368 | 3.7322 | 3.8271 | 3.9216 | 4.0158 | 4.1099
| S | Lmax |  | 4.2766 | m | [5 empty] | 2.9936 | 3.4213 | 3.849 | 4.2766 | 4.7043 | 5.132 | 5.5596 | 5.9582 | 6.324 | 6.7048 | 7.1016 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895
| Short | Wmin |  | 4.1316 | m | [5 empty] | 3.4295 | 3.6707 | 3.8989 | 4.1162 | 4.3246 | 4.5255 | 4.72 | 4.9091 | 5.0936 | 5.2741 | 5.4512 | 5.6254 | 5.7972 | 5.9669 | 6.1348 | 6.3013 | 6.4667 | 6.6311 | 6.7948 | 6.9581 | 7.121
|  | Wmax |  | 7.41 | m | [5 empty] | 5.187 | 5.928 | 6.669 | 7.41 | 8.151 | 8.892 | 9.633 | 10.3236 | 10.9575 | 11.6171 | 12.3048 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457
|  | L,W Vsp.min |  | 3.1374 | [6 empty] | 2.6042 | 2.7875 | 2.9607 | 3.1257 | 3.284 | 3.4365 | 3.5842 | 3.7278 | 3.8679 | 4.005 | 4.1395 | 4.2718 | 4.4023 | 4.5311 | 4.6586 | 4.7851 | 4.9106 | 5.0355 | 5.1598 | 5.2838 | 5.4075
|  | L,W Vsp.max |  | 6.0715 | [6 empty] | 4.836 | 5.2463 | 5.6566 | 6.0715 | 6.4944 | 6.9284 | 7.376 | 7.8395 | 8.3208 | 8.8218 | 9.344 | 9.889 | 10.4582 | 11.0529 | 11.6743 | 12.3236 | 13.002 | 13.7105 | 14.4501 | 15.2218 | 16.0265
|  | L,W throw max |  | 5.627 | [6 empty] | 3.9389 | 4.5016 | 5.0643 | 5.627 | 6.1897 | 6.7524 | 7.3151 | 7.8778 | 8.4405 | 9.0032 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595
|  | Lmin |  | 3.1374 | m | [5 empty] | 2.6042 | 2.7875 | 2.9607 | 3.1257 | 3.284 | 3.4365 | 3.5842 | 3.7278 | 3.8679 | 4.005 | 4.1395 | 4.2718 | 4.4023 | 4.5311 | 4.6586 | 4.7851 | 4.9106 | 5.0355 | 5.1598 | 5.2838 | 5.4075
216 | M | Lmax |  | 5.627 | m | [5 empty] | 3.9389 | 4.5016 | 5.0643 | 5.627 | 6.1897 | 6.7524 | 7.3151 | 7.8395 | 8.3208 | 8.8218 | 9.344 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595
(4-row) | Medium | Wmin |  | 3.1374 | m | [5 empty] | 2.6042 | 2.7875 | 2.9607 | 3.1257 | 3.284 | 3.4365 | 3.5842 | 3.7278 | 3.8679 | 4.005 | 4.1395 | 4.2718 | 4.4023 | 4.5311 | 4.6586 | 4.7851 | 4.9106 | 5.0355 | 5.1598 | 5.2838 | 5.4075
|  | Wmax |  | 5.627 | m | [5 empty] | 3.9389 | 4.5016 | 5.0643 | 5.627 | 6.1897 | 6.7524 | 7.3151 | 7.8395 | 8.3208 | 8.8218 | 9.344 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595
|  | L Vsp.min |  | 4.0956 | [6 empty] | 3.3996 | 3.6388 | 3.8649 | 4.0803 | 4.2869 | 4.486 | 4.6788 | 4.8663 | 5.0492 | 5.2281 | 5.4037 | 5.5764 | 5.7467 | 5.9149 | 6.0814 | 6.2464 | 6.4103 | 6.5733 | 6.7356 | 6.8975 | 7.059
|  | L Vsp.max |  | 7.9257 | [6 empty] | 6.3129 | 6.8485 | 7.3841 | 7.9257 | 8.4778 | 9.0444 | 9.6287 | 10.2337 | 10.862 | 11.5159 | 12.1976 | 12.9091 | 13.6521 | 14.4284 | 15.2396 | 16.0873 | 16.9728 | 17.8977 | 18.8631 | 19.8705 | 20.921
|  | L throw max |  | 7.3455 | [6 empty] | 5.1418 | 5.8764 | 6.6109 | 7.3455 | 8.08 | 8.8145 | 9.5491 | 10.2836 | 11.0182 | 11.7527 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485
|  | W Vsp.min |  | 2.3734 | [6 empty] | 1.9701 | 2.1087 | 2.2397 | 2.3646 | 2.4843 | 2.5997 | 2.7114 | 2.8201 | 2.926 | 3.0297 | 3.1315 | 3.2316 | 3.3303 | 3.4277 | 3.5242 | 3.6199 | 3.7148 | 3.8093 | 3.9034 | 3.9971 | 4.0907
|  | W Vsp.max |  | 4.593 | [6 empty] | 3.6584 | 3.9687 | 4.2792 | 4.593 | 4.913 | 5.2413 | 5.5799 | 5.9305 | 6.2946 | 6.6736 | 7.0686 | 7.4809 | 7.9115 | 8.3614 | 8.8315 | 9.3227 | 9.8359 | 10.3719 | 10.9313 | 11.5151 | 12.1239
|  | W throw max |  | 4.2567 | [6 empty] | 2.9797 | 3.4054 | 3.8311 | 4.2567 | 4.6824 | 5.1081 | 5.5338 | 5.9594 | 6.3851 | 6.8108 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561
|  | Lmin |  | 4.0956 | m | [5 empty] | 3.3996 | 3.6388 | 3.8649 | 4.0803 | 4.2869 | 4.486 | 4.6788 | 4.8663 | 5.0492 | 5.2281 | 5.4037 | 5.5764 | 5.7467 | 5.9149 | 6.0814 | 6.2464 | 6.4103 | 6.5733 | 6.7356 | 6.8975 | 7.059
| L | Lmax |  | 7.3455 | m | [5 empty] | 5.1418 | 5.8764 | 6.6109 | 7.3455 | 8.08 | 8.8145 | 9.5491 | 10.2337 | 10.862 | 11.5159 | 12.1976 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485
| Long | Wmin |  | 2.3734 | m | [5 empty] | 1.9701 | 2.1087 | 2.2397 | 2.3646 | 2.4843 | 2.5997 | 2.7114 | 2.8201 | 2.926 | 3.0297 | 3.1315 | 3.2316 | 3.3303 | 3.4277 | 3.5242 | 3.6199 | 3.7148 | 3.8093 | 3.9034 | 3.9971 | 4.0907
|  | Wmax |  | 4.2567 | m | [5 empty] | 2.9797 | 3.4054 | 3.8311 | 4.2567 | 4.6824 | 5.1081 | 5.5338 | 5.9305 | 6.2946 | 6.6736 | 7.0686 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561
[7 empty] | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240 | 250 | 260 | 270

## DN 950 (hidden)
| FACTORS: | K.l.min |  | 7
|  | K.l.max |  | 21
|  | K.dT |  | 1 | -12 K / dT
|  | K.H.min(sp) |  | 1.0037 | Increased draught risk as height increases, Fig 8, Krantz Layout Criteria TB 69 E
|  | K.H.max(vol) |  | 1 | Reduce max throw with height to maintain constant volume to prevent stagnation
|  | K.2D/3D |  | 1.1597 | Fig 8 / Fig 7 @ 0.25, Krantz Layout Criteria TB 69 E
|  | K.adpi |  | 0.94595 | Adjustment factor for ADPI
|  | v.room ≤ |  | 0.23665 | m/s, Krantz Layout Criteria TB 69 E
|  | K.h.min |  | 1.9
INPUT
|  |  | H.diffuser = | 2.5 | m | Height to Diffuser Centre-Line = 2.0 to 4.5 m
PMW- | L.neck |  | dT(cooling) = | -12 | K | dT = -8 K to -12 K
AD- | mm | ADPI ≥ 90% | ADPI ³ | 90 | % | 70%, 80%, 90% or 95%
DN 950 | 915 | = |  | 150 | L/s |  | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240 | 250 | 260 | 270 | 280 | 290 | 300 | 320 | 340 | 360 | 380 | 400
|  | Pt |  | 32.5417 | Pa |  | 3.4977 | 5.0646 | 6.9256 | 9.0822 | 11.5357 | 14.287 | 17.337 | 20.6868 | 24.337 | 28.2884 | 32.5417 | 37.0974 | 41.9563 | 47.1188 | [12 empty] | ≤ 20 | ≤ 30 | ≤ 40 | ≤ 50 | Pa
H.neck | Throw | Lw |  | 45.0967 | dB(A) |  | <15 | 15.7662 | 20.7006 | 24.9749 | 28.7452 | 32.1178 | 35.1686 | 37.9539 | 40.516 | 42.8882 | 45.0967 | 47.1626 | 49.1032 | 50.9328 | [12 empty] | ≤ 40 | ≤ 45 | ≤ 50 | ≤ 55 | dB(A)
mm | Setting | Lp* |  | 30.0967 | NC* |  | <5 | <5 | 5.7006 | 9.9749 | 13.7452 | 17.1178 | 20.1686 | 22.9539 | 25.516 | 27.8882 | 30.0967 | 32.1626 | 34.1032 | 35.9328 | [12 empty] | ≤ 25 | ≤ 30 | ≤ 35 | ≤ 40 | NC*
|  | L Vsp.min |  | 2.9999 |  |  | 50: 1.6726; 60: 1.8353; 70: 1.9864; 80: 2.1285; 90: 2.2637; 100: 2.3932; 110: 2.5183; 120: 2.6397; 130: 2.7582; 140: 2.8744; 150: 2.9887; 160: 3.1016; 170: 3.2134; 180: 3.3244
|  | L Vsp.max |  | 7.4165 |  |  | 50: 3.1012; 60: 3.467; 70: 3.8343; 80: 4.21; 90: 4.5991; 100: 5.0061; 110: 5.4343; 120: 5.8869; 130: 6.3666; 140: 6.8757; 150: 7.4165; 160: 7.991; 170: 8.6011; 180: 9.2487
|  | L throw max |  | 7.1895 |  |  | 50: 2.5082; 60: 3.0098; 70: 3.5115; 80: 4.0131; 90: 4.5147; 100: 5.0164; 110: 5.518; 120: 6.0196; 130: 6.5213; 140: 6.7393; 150: 6.8098; 160: 6.8803; 170: 6.9509; 180: 7.0214
|  | W Vsp.min |  | 5.1978 |  |  | 50: 2.898; 60: 3.18; 70: 3.4418; 80: 3.6881; 90: 3.9222; 100: 4.1466; 110: 4.3633; 120: 4.5737; 130: 4.7791; 140: 4.9804; 150: 5.1785; 160: 5.3741; 170: 5.5678; 180: 5.7602
|  | W Vsp.max |  | 12.8503 |  |  | 50: 5.3734; 60: 6.0072; 70: 6.6436; 80: 7.2945; 90: 7.9688; 100: 8.6739; 110: 9.4159; 120: 10.2001; 130: 11.0312; 140: 11.9133; 150: 12.8503; 160: 13.8458; 170: 14.903; 180: 16.0249
|  | W throw max |  | 12.457 |  |  | 50: 4.3459; 60: 5.215; 70: 6.0842; 80: 6.9534; 90: 7.8226; 100: 8.6917; 110: 9.5609; 120: 10.4301; 130: 11.2992; 140: 11.6769; 150: 11.7992; 160: 11.9214; 170: 12.0436; 180: 12.1659
|  | Hmin |  | 2.368 | m |  | 50: 2.1227; 60: 2.1472; 70: 2.1717; 80: 2.1963; 90: 2.2208; 100: 2.2453; 110: 2.2698; 120: 2.2944; 130: 2.3189; 140: 2.3434; 150: 2.368; 160: 2.3925; 170: 2.417; 180: 2.4416; 320: * for 10 dB room absorption
|  | Lmin |  | 2.9999 | m |  | 50: 1.6726; 60: 1.8353; 70: 1.9864; 80: 2.1285; 90: 2.2637; 100: 2.3932; 110: 2.5183; 120: 2.6397; 130: 2.7582; 140: 2.8744; 150: 2.9887; 160: 3.1016; 170: 3.2134; 180: 3.3244
| S | Lmax |  | 7.1895 | m |  | 50: 2.5082; 60: 3.0098; 70: 3.5115; 80: 4.0131; 90: 4.5147; 100: 5.0061; 110: 5.4343; 120: 5.8869; 130: 6.3666; 140: 6.7393; 150: 6.8098; 160: 6.8803; 170: 6.9509; 180: 7.0214
| Short | Wmin |  | 5.1978 | m |  | 50: 2.898; 60: 3.18; 70: 3.4418; 80: 3.6881; 90: 3.9222; 100: 4.1466; 110: 4.3633; 120: 4.5737; 130: 4.7791; 140: 4.9804; 150: 5.1785; 160: 5.3741; 170: 5.5678; 180: 5.7602
|  | Wmax |  | 12.457 | m |  | 50: 4.3459; 60: 5.215; 70: 6.0842; 80: 6.9534; 90: 7.8226; 100: 8.6739; 110: 9.4159; 120: 10.2001; 130: 11.0312; 140: 11.6769; 150: 11.7992; 160: 11.9214; 170: 12.0436; 180: 12.1659
|  | L,W Vsp.min |  | 3.9471 |  |  | 50: 2.2007; 60: 2.4148; 70: 2.6136; 80: 2.8006; 90: 2.9784; 100: 3.1488; 110: 3.3134; 120: 3.4732; 130: 3.6291; 140: 3.782; 150: 3.9324; 160: 4.0809; 170: 4.228; 180: 4.3741
|  | L,W Vsp.max |  | 9.7582 |  |  | 50: 4.0805; 60: 4.5617; 70: 5.045; 80: 5.5392; 90: 6.0513; 100: 6.5867; 110: 7.1502; 120: 7.7457; 130: 8.3768; 140: 9.0467; 150: 9.7582; 160: 10.5141; 170: 11.3169; 180: 12.1689
|  | L,W throw max |  | 9.4595 |  |  | 50: 3.3001; 60: 3.9602; 70: 4.6202; 80: 5.2802; 90: 5.9402; 100: 6.6003; 110: 7.2603; 120: 7.9203; 130: 8.5803; 140: 8.8671; 150: 8.96; 160: 9.0528; 170: 9.1456; 180: 9.2384
|  | Lmin |  | 3.9471 | m |  | 50: 2.2007; 60: 2.4148; 70: 2.6136; 80: 2.8006; 90: 2.9784; 100: 3.1488; 110: 3.3134; 120: 3.4732; 130: 3.6291; 140: 3.782; 150: 3.9324; 160: 4.0809; 170: 4.228; 180: 4.3741
99 | M | Lmax |  | 9.4595 | m |  | 50: 3.3001; 60: 3.9602; 70: 4.6202; 80: 5.2802; 90: 5.9402; 100: 6.5867; 110: 7.1502; 120: 7.7457; 130: 8.3768; 140: 8.8671; 150: 8.96; 160: 9.0528; 170: 9.1456; 180: 9.2384
(1-row) | Medium | Wmin |  | 3.9471 | m |  | 50: 2.2007; 60: 2.4148; 70: 2.6136; 80: 2.8006; 90: 2.9784; 100: 3.1488; 110: 3.3134; 120: 3.4732; 130: 3.6291; 140: 3.782; 150: 3.9324; 160: 4.0809; 170: 4.228; 180: 4.3741
|  | Wmax |  | 9.4595 | m |  | 50: 3.3001; 60: 3.9602; 70: 4.6202; 80: 5.2802; 90: 5.9402; 100: 6.5867; 110: 7.1502; 120: 7.7457; 130: 8.3768; 140: 8.8671; 150: 8.96; 160: 9.0528; 170: 9.1456; 180: 9.2384
|  | L Vsp.min |  | 5.1525 |  |  | 50: 2.8728; 60: 3.1523; 70: 3.4118; 80: 3.6559; 90: 3.888; 100: 4.1105; 110: 4.3253; 120: 4.5339; 130: 4.7375; 140: 4.937; 150: 5.1334; 160: 5.3272; 170: 5.5193; 180: 5.71
|  | L Vsp.max |  | 12.7384 |  |  | 50: 5.3266; 60: 5.9549; 70: 6.5857; 80: 7.2309; 90: 7.8994; 100: 8.5983; 110: 9.3339; 120: 10.1112; 130: 10.9351; 140: 11.8095; 150: 12.7384; 160: 13.7251; 170: 14.7731; 180: 15.8853
|  | L throw max |  | 12.3485 |  |  | 50: 4.308; 60: 5.1696; 70: 6.0312; 80: 6.8928; 90: 7.7544; 100: 8.616; 110: 9.4776; 120: 10.3392; 130: 11.2008; 140: 11.5752; 150: 11.6963; 160: 11.8175; 170: 11.9387; 180: 12.0599
|  | W Vsp.min |  | 2.9859 |  |  | 50: 1.6648; 60: 1.8268; 70: 1.9772; 80: 2.1186; 90: 2.2531; 100: 2.3821; 110: 2.5065; 120: 2.6274; 130: 2.7454; 140: 2.861; 150: 2.9748; 160: 3.0872; 170: 3.1985; 180: 3.309
|  | W Vsp.max |  | 7.382 |  |  | 50: 3.0868; 60: 3.4509; 70: 3.8165; 80: 4.1904; 90: 4.5777; 100: 4.9828; 110: 5.4091; 120: 5.8595; 130: 6.337; 140: 6.8437; 150: 7.382; 160: 7.9538; 170: 8.5611; 180: 9.2057
|  | W throw max |  | 7.1561 |  |  | 50: 2.4965; 60: 2.9958; 70: 3.4951; 80: 3.9944; 90: 4.4937; 100: 4.993; 110: 5.4923; 120: 5.9916; 130: 6.4909; 140: 6.7079; 150: 6.7781; 160: 6.8483; 170: 6.9186; 180: 6.9888
|  | Lmin |  | 5.1525 | m |  | 50: 2.8728; 60: 3.1523; 70: 3.4118; 80: 3.6559; 90: 3.888; 100: 4.1105; 110: 4.3253; 120: 4.5339; 130: 4.7375; 140: 4.937; 150: 5.1334; 160: 5.3272; 170: 5.5193; 180: 5.71
| L | Lmax |  | 12.3485 | m |  | 50: 4.308; 60: 5.1696; 70: 6.0312; 80: 6.8928; 90: 7.7544; 100: 8.5983; 110: 9.3339; 120: 10.1112; 130: 10.9351; 140: 11.5752; 150: 11.6963; 160: 11.8175; 170: 11.9387; 180: 12.0599
| Long | Wmin |  | 2.9859 | m |  | 50: 1.6648; 60: 1.8268; 70: 1.9772; 80: 2.1186; 90: 2.2531; 100: 2.3821; 110: 2.5065; 120: 2.6274; 130: 2.7454; 140: 2.861; 150: 2.9748; 160: 3.0872; 170: 3.1985; 180: 3.309
|  | Wmax |  | 7.1561 | m |  | 50: 2.4965; 60: 2.9958; 70: 3.4951; 80: 3.9944; 90: 4.4937; 100: 4.9828; 110: 5.4091; 120: 5.8595; 130: 6.337; 140: 6.7079; 150: 6.7781; 160: 6.8483; 170: 6.9186; 180: 6.9888
|  | Pt |  | 16.5804 | Pa |  |  |  | 3.5287 | 4.6275 | 5.8776 | 7.2794 | 8.8335 | 10.5402 | 12.4001 | 14.4133 | 16.5804 | 18.9017 | 21.3773 | 24.0077 | 26.793 | 29.7336 | 32.8296 | 36.0813 | 39.4889 | 43.0527 | 46.7728
H.neck | Throw | Lw |  | 35.9075 | dB(A) |  |  |  | <15 | 15.7858 | 19.556 | 22.9286 | 25.9795 | 28.7647 | 31.3269 | 33.6991 | 35.9075 | 37.9734 | 39.914 | 41.7436 | 43.4743 | 45.1162 | 46.678 | 48.1671 | 49.59 | 50.9524 | 52.2591
mm | Setting | Lp* |  | 20.9075 | NC* |  |  |  | <5 | <5 | <5 | 7.9286 | 10.9795 | 13.7647 | 16.3269 | 18.6991 | 20.9075 | 22.9734 | 24.914 | 26.7436 | 28.4743 | 30.1162 | 31.678 | 33.1671 | 34.59 | 35.9524 | 37.2591
|  | L Vsp.min |  | 2.9493 |  |  |  |  | 1.9865 | 2.1262 | 2.2582 | 2.384 | 2.5046 | 2.6208 | 2.7333 | 2.8426 | 2.9493 | 3.0536 | 3.1559 | 3.2566 | 3.3557 | 3.4537 | 3.5506 | 3.6466 | 3.742 | 3.8367 | 3.9311
|  | L Vsp.max |  | 6.2927 |  |  |  |  | 3.6709 | 3.9809 | 4.2906 | 4.6032 | 4.9216 | 5.2479 | 5.5841 | 5.9319 | 6.2927 | 6.6678 | 7.0586 | 7.4661 | 7.8914 | 8.3355 | 8.7993 | 9.2836 | 9.7894 | 10.3173 | 10.8682
|  | L throw max |  | 6.3732 |  |  |  |  | 2.9742 | 3.399 | 3.8239 | 4.2488 | 4.6737 | 5.0986 | 5.5235 | 5.9483 | 6.3732 | 6.7981 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895
|  | W Vsp.min |  | 5.1101 |  |  |  |  | 3.4419 | 3.684 | 3.9127 | 4.1307 | 4.3396 | 4.541 | 4.7359 | 4.9253 | 5.1101 | 5.2909 | 5.4682 | 5.6426 | 5.8144 | 5.9841 | 6.152 | 6.3184 | 6.4836 | 6.6478 | 6.8113
|  | W Vsp.max |  | 10.9031 |  |  |  |  | 6.3605 | 6.8976 | 7.4341 | 7.9759 | 8.5275 | 9.093 | 9.6755 | 10.278 | 10.9031 | 11.5532 | 12.2303 | 12.9364 | 13.6733 | 14.4427 | 15.2463 | 16.0855 | 16.9618 | 17.8765 | 18.8311
|  | W throw max |  | 11.0427 |  |  |  |  | 5.1533 | 5.8894 | 6.6256 | 7.3618 | 8.098 | 8.8342 | 9.5703 | 10.3065 | 11.0427 | 11.7789 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457
|  | Hmin |  | 2.368 | m |  |  |  | 2.1717 | 2.1963 | 2.2208 | 2.2453 | 2.2698 | 2.2944 | 2.3189 | 2.3434 | 2.368 | 2.3925 | 2.417 | 2.4416 | 2.4661 | 2.4906 | 2.5152 | 2.5397 | 2.5642 | 2.5888 | 2.6133
|  | Lmin |  | 2.9493 | m |  |  |  | 1.9865 | 2.1262 | 2.2582 | 2.384 | 2.5046 | 2.6208 | 2.7333 | 2.8426 | 2.9493 | 3.0536 | 3.1559 | 3.2566 | 3.3557 | 3.4537 | 3.5506 | 3.6466 | 3.742 | 3.8367 | 3.9311
| S | Lmax |  | 6.2927 | m |  |  |  | 2.9742 | 3.399 | 3.8239 | 4.2488 | 4.6737 | 5.0986 | 5.5235 | 5.9319 | 6.2927 | 6.6678 | 7.0586 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895
| Short | Wmin |  | 5.1101 | m |  |  |  | 3.4419 | 3.684 | 3.9127 | 4.1307 | 4.3396 | 4.541 | 4.7359 | 4.9253 | 5.1101 | 5.2909 | 5.4682 | 5.6426 | 5.8144 | 5.9841 | 6.152 | 6.3184 | 6.4836 | 6.6478 | 6.8113
|  | Wmax |  | 10.9031 | m |  |  |  | 5.1533 | 5.8894 | 6.6256 | 7.3618 | 8.098 | 8.8342 | 9.5703 | 10.278 | 10.9031 | 11.5532 | 12.2303 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457
|  | L,W Vsp.min |  | 3.8805 |  |  |  |  | 2.6137 | 2.7975 | 2.9712 | 3.1367 | 3.2954 | 3.4483 | 3.5963 | 3.7402 | 3.8805 | 4.0178 | 4.1524 | 4.2848 | 4.4153 | 4.5442 | 4.6717 | 4.798 | 4.9235 | 5.0482 | 5.1723
|  | L,W Vsp.max |  | 8.2795 |  |  |  |  | 4.83 | 5.2378 | 5.6453 | 6.0567 | 6.4756 | 6.905 | 7.3473 | 7.8048 | 8.2795 | 8.7732 | 9.2873 | 9.8235 | 10.3831 | 10.9674 | 11.5776 | 12.2149 | 12.8803 | 13.575 | 14.2998
|  | L,W throw max |  | 8.3855 |  |  |  |  | 3.9132 | 4.4723 | 5.0313 | 5.5904 | 6.1494 | 6.7084 | 7.2675 | 7.8265 | 8.3855 | 8.9446 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595
|  | Lmin |  | 3.8805 | m |  |  |  | 2.6137 | 2.7975 | 2.9712 | 3.1367 | 3.2954 | 3.4483 | 3.5963 | 3.7402 | 3.8805 | 4.0178 | 4.1524 | 4.2848 | 4.4153 | 4.5442 | 4.6717 | 4.798 | 4.9235 | 5.0482 | 5.1723
138 | M | Lmax |  | 8.2795 | m |  |  |  | 3.9132 | 4.4723 | 5.0313 | 5.5904 | 6.1494 | 6.7084 | 7.2675 | 7.8048 | 8.2795 | 8.7732 | 9.2873 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595
(2-row) | Medium | Wmin |  | 3.8805 | m |  |  |  | 2.6137 | 2.7975 | 2.9712 | 3.1367 | 3.2954 | 3.4483 | 3.5963 | 3.7402 | 3.8805 | 4.0178 | 4.1524 | 4.2848 | 4.4153 | 4.5442 | 4.6717 | 4.798 | 4.9235 | 5.0482 | 5.1723
|  | Wmax |  | 8.2795 | m |  |  |  | 3.9132 | 4.4723 | 5.0313 | 5.5904 | 6.1494 | 6.7084 | 7.2675 | 7.8048 | 8.2795 | 8.7732 | 9.2873 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595
|  | L Vsp.min |  | 5.0656 |  |  |  |  | 3.4119 | 3.6518 | 3.8786 | 4.0947 | 4.3018 | 4.5014 | 4.6946 | 4.8824 | 5.0656 | 5.2448 | 5.4206 | 5.5934 | 5.7637 | 5.932 | 6.0984 | 6.2634 | 6.4271 | 6.5899 | 6.7519
|  | L Vsp.max |  | 10.8081 |  |  |  |  | 6.3051 | 6.8375 | 7.3693 | 7.9064 | 8.4532 | 9.0137 | 9.5912 | 10.1884 | 10.8081 | 11.4525 | 12.1237 | 12.8236 | 13.5541 | 14.3169 | 15.1134 | 15.9453 | 16.814 | 17.7208 | 18.667
|  | L throw max |  | 10.9465 |  |  |  |  | 5.1084 | 5.8381 | 6.5679 | 7.2977 | 8.0274 | 8.7572 | 9.4869 | 10.2167 | 10.9465 | 11.6762 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485
|  | W Vsp.min |  | 2.9356 |  |  |  |  | 1.9772 | 2.1163 | 2.2477 | 2.3729 | 2.4929 | 2.6086 | 2.7206 | 2.8294 | 2.9356 | 3.0394 | 3.1413 | 3.2414 | 3.3401 | 3.4376 | 3.5341 | 3.6297 | 3.7246 | 3.8189 | 3.9128
|  | W Vsp.max |  | 6.2634 |  |  |  |  | 3.6539 | 3.9624 | 4.2706 | 4.5818 | 4.8987 | 5.2235 | 5.5582 | 5.9043 | 6.2634 | 6.6368 | 7.0258 | 7.4314 | 7.8547 | 8.2967 | 8.7584 | 9.2404 | 9.7438 | 10.2693 | 10.8177
|  | W throw max |  | 6.3436 |  |  |  |  | 2.9603 | 3.3832 | 3.8061 | 4.229 | 4.652 | 5.0749 | 5.4978 | 5.9207 | 6.3436 | 6.7665 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561
|  | Lmin |  | 5.0656 | m |  |  |  | 3.4119 | 3.6518 | 3.8786 | 4.0947 | 4.3018 | 4.5014 | 4.6946 | 4.8824 | 5.0656 | 5.2448 | 5.4206 | 5.5934 | 5.7637 | 5.932 | 6.0984 | 6.2634 | 6.4271 | 6.5899 | 6.7519
| L | Lmax |  | 10.8081 | m |  |  |  | 5.1084 | 5.8381 | 6.5679 | 7.2977 | 8.0274 | 8.7572 | 9.4869 | 10.1884 | 10.8081 | 11.4525 | 12.1237 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485
| Long | Wmin |  | 2.9356 | m |  |  |  | 1.9772 | 2.1163 | 2.2477 | 2.3729 | 2.4929 | 2.6086 | 2.7206 | 2.8294 | 2.9356 | 3.0394 | 3.1413 | 3.2414 | 3.3401 | 3.4376 | 3.5341 | 3.6297 | 3.7246 | 3.8189 | 3.9128
|  | Wmax |  | 6.2634 | m |  |  |  | 2.9603 | 3.3832 | 3.8061 | 4.229 | 4.652 | 5.0749 | 5.4978 | 5.9043 | 6.2634 | 6.6368 | 7.0258 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561
|  | Pt |  | 10.0033 | Pa | [5 empty] | 3.5461 | 4.3918 | 5.3294 | 6.3591 | 7.4812 | 8.6958 | 10.0033 | 11.4037 | 12.8973 | 14.4843 | 16.1647 | 17.9388 | 19.8067 | 21.7685 | 23.8244 | 25.9745 | 28.2189 | 30.5578 | 32.9912 | 35.5192 | 38.142 | 40.8596 | 46.5799
H.neck | Throw | Lw |  | 29.0213 | dB(A) | [5 empty] | <15 | 16.0424 | 19.0933 | 21.8785 | 24.4407 | 26.8129 | 29.0213 | 31.0872 | 33.0278 | 34.8574 | 36.5881 | 38.23 | 39.7918 | 41.2809 | 42.7038 | 44.0661 | 45.3728 | 46.6283 | 47.8364 | 49.0005 | 50.1238 | 51.209 | 53.2748
mm | Setting | Lp* |  | 14.0213 | NC* | [5 empty] | <5 | <5 | <5 | 6.8785 | 9.4407 | 11.8129 | 14.0213 | 16.0872 | 18.0278 | 19.8574 | 21.5881 | 23.23 | 24.7918 | 26.2809 | 27.7038 | 29.0661 | 30.3728 | 31.6283 | 32.8364 | 34.0005 | 35.1238 | 36.209 | 38.2748
|  | L Vsp.min |  | 2.9284 | [6 empty] | 2.2525 | 2.3765 | 2.4951 | 2.6089 | 2.7188 | 2.8251 | 2.9284 | 3.029 | 3.1273 | 3.2235 | 3.3178 | 3.4105 | 3.5017 | 3.5917 | 3.6805 | 3.7682 | 3.8551 | 3.9412 | 4.0267 | 4.1115 | 4.1959 | 4.2798 | 4.4466
|  | L Vsp.max |  | 5.8296 | [6 empty] | 4.1634 | 4.4372 | 4.7103 | 4.9846 | 5.2617 | 5.543 | 5.8296 | 6.1226 | 6.423 | 6.7316 | 7.0492 | 7.3766 | 7.7144 | 8.0632 | 8.4236 | 8.7963 | 9.1817 | 9.5803 | 9.9927 | 10.4193 | 10.8605 | 11.3167 | 12.2761
|  | L throw max |  | 5.6274 | [6 empty] | 3.3765 | 3.7516 | 4.1268 | 4.502 | 4.8771 | 5.2523 | 5.6274 | 6.0026 | 6.3778 | 6.7529 | 7.1281 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895
|  | W Vsp.min |  | 5.074 | [6 empty] | 3.9028 | 4.1177 | 4.3231 | 4.5204 | 4.7107 | 4.895 | 5.074 | 5.2483 | 5.4186 | 5.5852 | 5.7487 | 5.9093 | 6.0674 | 6.2232 | 6.377 | 6.5291 | 6.6797 | 6.8289 | 6.9769 | 7.1239 | 7.2701 | 7.4154 | 7.7045
|  | W Vsp.max |  | 10.1007 | [6 empty] | 7.2138 | 7.6883 | 8.1615 | 8.6367 | 9.1168 | 9.6041 | 10.1007 | 10.6084 | 11.1289 | 11.6636 | 12.214 | 12.7812 | 13.3665 | 13.9709 | 14.5954 | 15.2411 | 15.9089 | 16.5996 | 17.3141 | 18.0532 | 18.8176 | 19.6082 | 21.2706
|  | W throw max |  | 9.7505 | [6 empty] | 5.8503 | 6.5004 | 7.1504 | 7.8004 | 8.4505 | 9.1005 | 9.7505 | 10.4006 | 11.0506 | 11.7006 | 12.3507 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457
|  | Hmin |  | 2.368 | m | [5 empty] | 2.2208 | 2.2453 | 2.2698 | 2.2944 | 2.3189 | 2.3434 | 2.368 | 2.3925 | 2.417 | 2.4416 | 2.4661 | 2.4906 | 2.5152 | 2.5397 | 2.5642 | 2.5888 | 2.6133 | 2.6378 | 2.6623 | 2.6869 | 2.7114 | 2.7359 | 2.785
|  | Lmin |  | 2.9284 | m | [5 empty] | 2.2525 | 2.3765 | 2.4951 | 2.6089 | 2.7188 | 2.8251 | 2.9284 | 3.029 | 3.1273 | 3.2235 | 3.3178 | 3.4105 | 3.5017 | 3.5917 | 3.6805 | 3.7682 | 3.8551 | 3.9412 | 4.0267 | 4.1115 | 4.1959 | 4.2798 | 4.4466
| S | Lmax |  | 5.6274 | m | [5 empty] | 3.3765 | 3.7516 | 4.1268 | 4.502 | 4.8771 | 5.2523 | 5.6274 | 6.0026 | 6.3778 | 6.7316 | 7.0492 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895
| Short | Wmin |  | 5.074 | m | [5 empty] | 3.9028 | 4.1177 | 4.3231 | 4.5204 | 4.7107 | 4.895 | 5.074 | 5.2483 | 5.4186 | 5.5852 | 5.7487 | 5.9093 | 6.0674 | 6.2232 | 6.377 | 6.5291 | 6.6797 | 6.8289 | 6.9769 | 7.1239 | 7.2701 | 7.4154 | 7.7045
|  | Wmax |  | 9.7505 | m | [5 empty] | 5.8503 | 6.5004 | 7.1504 | 7.8004 | 8.4505 | 9.1005 | 9.7505 | 10.4006 | 11.0506 | 11.6636 | 12.214 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457
|  | L,W Vsp.min |  | 3.8531 | [6 empty] | 2.9637 | 3.1269 | 3.2829 | 3.4327 | 3.5772 | 3.7171 | 3.8531 | 3.9855 | 4.1147 | 4.2413 | 4.3654 | 4.4874 | 4.6074 | 4.7257 | 4.8426 | 4.9581 | 5.0724 | 5.1857 | 5.2981 | 5.4097 | 5.5207 | 5.6311 | 5.8506
|  | L,W Vsp.max |  | 7.6702 | [6 empty] | 5.478 | 5.8383 | 6.1976 | 6.5585 | 6.9231 | 7.2931 | 7.6702 | 8.0558 | 8.451 | 8.8571 | 9.275 | 9.7057 | 10.1501 | 10.6091 | 11.0834 | 11.5737 | 12.0808 | 12.6053 | 13.1479 | 13.7091 | 14.2896 | 14.89 | 16.1523
|  | L,W throw max |  | 7.4043 | [6 empty] | 4.4426 | 4.9362 | 5.4298 | 5.9234 | 6.4171 | 6.9107 | 7.4043 | 7.8979 | 8.3915 | 8.8852 | 9.3788 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595
|  | Lmin |  | 3.8531 | m | [5 empty] | 2.9637 | 3.1269 | 3.2829 | 3.4327 | 3.5772 | 3.7171 | 3.8531 | 3.9855 | 4.1147 | 4.2413 | 4.3654 | 4.4874 | 4.6074 | 4.7257 | 4.8426 | 4.9581 | 5.0724 | 5.1857 | 5.2981 | 5.4097 | 5.5207 | 5.6311 | 5.8506
177 | M | Lmax |  | 7.4043 | m | [5 empty] | 4.4426 | 4.9362 | 5.4298 | 5.9234 | 6.4171 | 6.9107 | 7.4043 | 7.8979 | 8.3915 | 8.8571 | 9.275 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595
(3-row) | Medium | Wmin |  | 3.8531 | m | [5 empty] | 2.9637 | 3.1269 | 3.2829 | 3.4327 | 3.5772 | 3.7171 | 3.8531 | 3.9855 | 4.1147 | 4.2413 | 4.3654 | 4.4874 | 4.6074 | 4.7257 | 4.8426 | 4.9581 | 5.0724 | 5.1857 | 5.2981 | 5.4097 | 5.5207 | 5.6311 | 5.8506
|  | Wmax |  | 7.4043 | m | [5 empty] | 4.4426 | 4.9362 | 5.4298 | 5.9234 | 6.4171 | 6.9107 | 7.4043 | 7.8979 | 8.3915 | 8.8571 | 9.275 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595
|  | L Vsp.min |  | 5.0298 | [6 empty] | 3.8688 | 4.0818 | 4.2854 | 4.481 | 4.6697 | 4.8523 | 5.0298 | 5.2026 | 5.3714 | 5.5366 | 5.6986 | 5.8578 | 6.0145 | 6.169 | 6.3215 | 6.4722 | 6.6215 | 6.7694 | 6.9161 | 7.0618 | 7.2067 | 7.3508 | 7.6374
|  | L Vsp.max |  | 10.0127 | [6 empty] | 7.1509 | 7.6213 | 8.0903 | 8.5615 | 9.0374 | 9.5205 | 10.0127 | 10.516 | 11.0319 | 11.562 | 12.1076 | 12.6698 | 13.25 | 13.8491 | 14.4682 | 15.1083 | 15.7703 | 16.455 | 17.1632 | 17.8959 | 18.6537 | 19.4374 | 21.0852
|  | L throw max |  | 9.6656 | [6 empty] | 5.7993 | 6.4437 | 7.0881 | 7.7325 | 8.3768 | 9.0212 | 9.6656 | 10.3099 | 10.9543 | 11.5987 | 12.2431 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485
|  | W Vsp.min |  | 2.9148 | [6 empty] | 2.242 | 2.3655 | 2.4835 | 2.5968 | 2.7061 | 2.812 | 2.9148 | 3.015 | 3.1128 | 3.2085 | 3.3024 | 3.3946 | 3.4854 | 3.575 | 3.6633 | 3.7507 | 3.8372 | 3.9229 | 4.0079 | 4.0924 | 4.1763 | 4.2599 | 4.4259
|  | W Vsp.max |  | 5.8025 | [6 empty] | 4.144 | 4.4166 | 4.6884 | 4.9614 | 5.2372 | 5.5172 | 5.8025 | 6.0941 | 6.3931 | 6.7003 | 7.0164 | 7.3423 | 7.6785 | 8.0257 | 8.3845 | 8.7554 | 9.139 | 9.5358 | 9.9462 | 10.3708 | 10.81 | 11.2641 | 12.219
|  | W throw max |  | 5.6013 | [6 empty] | 3.3608 | 3.7342 | 4.1076 | 4.481 | 4.8544 | 5.2279 | 5.6013 | 5.9747 | 6.3481 | 6.7215 | 7.0949 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561
|  | Lmin |  | 5.0298 | m | [5 empty] | 3.8688 | 4.0818 | 4.2854 | 4.481 | 4.6697 | 4.8523 | 5.0298 | 5.2026 | 5.3714 | 5.5366 | 5.6986 | 5.8578 | 6.0145 | 6.169 | 6.3215 | 6.4722 | 6.6215 | 6.7694 | 6.9161 | 7.0618 | 7.2067 | 7.3508 | 7.6374
| L | Lmax |  | 9.6656 | m | [5 empty] | 5.7993 | 6.4437 | 7.0881 | 7.7325 | 8.3768 | 9.0212 | 9.6656 | 10.3099 | 10.9543 | 11.562 | 12.1076 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485
| Long | Wmin |  | 2.9148 | m | [5 empty] | 2.242 | 2.3655 | 2.4835 | 2.5968 | 2.7061 | 2.812 | 2.9148 | 3.015 | 3.1128 | 3.2085 | 3.3024 | 3.3946 | 3.4854 | 3.575 | 3.6633 | 3.7507 | 3.8372 | 3.9229 | 4.0079 | 4.0924 | 4.1763 | 4.2599 | 4.4259
|  | Wmax |  | 5.6013 | m | [5 empty] | 3.3608 | 3.7342 | 4.1076 | 4.481 | 4.8544 | 5.2279 | 5.6013 | 5.9747 | 6.3481 | 6.7003 | 7.0164 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561
|  | Pt |  | 6.6768 | Pa | [7 empty] | 3.5572 | 4.2445 | 4.9934 | 5.8042 | 6.6768 | 7.6116 | 8.6085 | 9.6677 | 10.7894 | 11.9735 | 13.2203 | 14.5297 | 15.9019 | 17.337 | 18.8351 | 20.3962 | 22.0204 | 23.7078 | 25.4584 | 27.2723 | 31.0904 | 35.1624 | 39.4889 | 44.0704 | 48.9072
H.neck | Throw | Lw |  | 23.512 | dB(A) | [7 empty] | <15 | 16.3692 | 18.9314 | 21.3035 | 23.512 | 25.5779 | 27.5185 | 29.3481 | 31.0788 | 32.7207 | 34.2825 | 35.7716 | 37.1945 | 38.5568 | 39.8635 | 41.119 | 42.3271 | 43.4912 | 44.6145 | 45.6997 | 47.7655 | 49.7061 | 51.5358 | 53.2665 | 54.9084
mm | Setting | Lp* |  | 8.512 | NC* | [7 empty] | <5 | <5 | <5 | 6.3035 | 8.512 | 10.5779 | 12.5185 | 14.3481 | 16.0788 | 17.7207 | 19.2825 | 20.7716 | 22.1945 | 23.5568 | 24.8635 | 26.119 | 27.3271 | 28.4912 | 29.6145 | 30.6997 | 32.7655 | 34.7061 | 36.5358 | 38.2665 | 39.9084
|  | L Vsp.min |  | 2.9179 | [8 empty] | 2.4902 | 2.6029 | 2.7114 | 2.8163 | 2.9179 | 3.0166 | 3.1128 | 3.2068 | 3.2986 | 3.3887 | 3.477 | 3.5639 | 3.6494 | 3.7336 | 3.8167 | 3.8988 | 3.98 | 4.0603 | 4.1399 | 4.2188 | 4.3749 | 4.529 | 4.6815 | 4.8329 | 4.9835
|  | L Vsp.max |  | 5.5954 | [8 empty] | 4.6035 | 4.8515 | 5.0986 | 5.3463 | 5.5954 | 5.8468 | 6.1015 | 6.3601 | 6.6233 | 6.8916 | 7.1656 | 7.4459 | 7.7329 | 8.027 | 8.3287 | 8.6384 | 8.9564 | 9.283 | 9.6187 | 9.9638 | 10.6832 | 11.4437 | 12.2474 | 13.0964 | 13.9927
|  | L throw max |  | 5.0941 | [8 empty] | 3.7357 | 4.0753 | 4.4149 | 4.7545 | 5.0941 | 5.4338 | 5.7734 | 6.113 | 6.4526 | 6.7922 | 7.1318 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895
|  | W Vsp.min |  | 5.0557 | [8 empty] | 4.3148 | 4.51 | 4.698 | 4.8797 | 5.0557 | 5.2268 | 5.3935 | 5.5563 | 5.7154 | 5.8714 | 6.0245 | 6.175 | 6.3231 | 6.4691 | 6.6131 | 6.7554 | 6.8961 | 7.0353 | 7.1732 | 7.3099 | 7.5803 | 7.8472 | 8.1116 | 8.3739 | 8.6348
|  | W Vsp.max |  | 9.6949 | [8 empty] | 7.9763 | 8.406 | 8.8343 | 9.2633 | 9.6949 | 10.1306 | 10.5719 | 11.02 | 11.4759 | 11.9409 | 12.4157 | 12.9014 | 13.3986 | 13.9082 | 14.431 | 14.9675 | 15.5185 | 16.0845 | 16.6661 | 17.264 | 18.5105 | 19.8281 | 21.2207 | 22.6918 | 24.2448
|  | W throw max |  | 8.8265 | [8 empty] | 6.4728 | 7.0612 | 7.6496 | 8.2381 | 8.8265 | 9.4149 | 10.0034 | 10.5918 | 11.1802 | 11.7687 | 12.3571 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457
|  | Hmin |  | 2.368 | m | [7 empty] | 2.2698 | 2.2944 | 2.3189 | 2.3434 | 2.368 | 2.3925 | 2.417 | 2.4416 | 2.4661 | 2.4906 | 2.5152 | 2.5397 | 2.5642 | 2.5888 | 2.6133 | 2.6378 | 2.6623 | 2.6869 | 2.7114 | 2.7359 | 2.785 | 2.8341 | 2.8831 | 2.9322 | 2.9813
|  | Lmin |  | 2.9179 | m | [7 empty] | 2.4902 | 2.6029 | 2.7114 | 2.8163 | 2.9179 | 3.0166 | 3.1128 | 3.2068 | 3.2986 | 3.3887 | 3.477 | 3.5639 | 3.6494 | 3.7336 | 3.8167 | 3.8988 | 3.98 | 4.0603 | 4.1399 | 4.2188 | 4.3749 | 4.529 | 4.6815 | 4.8329 | 4.9835
| S | Lmax |  | 5.0941 | m | [7 empty] | 3.7357 | 4.0753 | 4.4149 | 4.7545 | 5.0941 | 5.4338 | 5.7734 | 6.113 | 6.4526 | 6.7922 | 7.1318 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895
| Short | Wmin |  | 5.0557 | m | [7 empty] | 4.3148 | 4.51 | 4.698 | 4.8797 | 5.0557 | 5.2268 | 5.3935 | 5.5563 | 5.7154 | 5.8714 | 6.0245 | 6.175 | 6.3231 | 6.4691 | 6.6131 | 6.7554 | 6.8961 | 7.0353 | 7.1732 | 7.3099 | 7.5803 | 7.8472 | 8.1116 | 8.3739 | 8.6348
|  | Wmax |  | 8.8265 | m | [7 empty] | 6.4728 | 7.0612 | 7.6496 | 8.2381 | 8.8265 | 9.4149 | 10.0034 | 10.5918 | 11.1802 | 11.7687 | 12.3571 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457
|  | L,W Vsp.min |  | 3.8392 | [8 empty] | 3.2765 | 3.4248 | 3.5675 | 3.7055 | 3.8392 | 3.9691 | 4.0957 | 4.2193 | 4.3402 | 4.4586 | 4.5749 | 4.6892 | 4.8016 | 4.9125 | 5.0218 | 5.1299 | 5.2367 | 5.3424 | 5.4471 | 5.5509 | 5.7562 | 5.959 | 6.1597 | 6.3589 | 6.5571
|  | L,W Vsp.max |  | 7.3621 | [8 empty] | 6.057 | 6.3833 | 6.7085 | 7.0343 | 7.3621 | 7.6929 | 8.028 | 8.3683 | 8.7145 | 9.0676 | 9.4282 | 9.7969 | 10.1745 | 10.5615 | 10.9585 | 11.3659 | 11.7843 | 12.2141 | 12.6558 | 13.1098 | 14.0564 | 15.057 | 16.1144 | 17.2315 | 18.4109
|  | L,W throw max |  | 6.7026 | [8 empty] | 4.9152 | 5.3621 | 5.8089 | 6.2558 | 6.7026 | 7.1494 | 7.5963 | 8.0431 | 8.49 | 8.9368 | 9.3836 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595
|  | Lmin |  | 3.8392 | m | [7 empty] | 3.2765 | 3.4248 | 3.5675 | 3.7055 | 3.8392 | 3.9691 | 4.0957 | 4.2193 | 4.3402 | 4.4586 | 4.5749 | 4.6892 | 4.8016 | 4.9125 | 5.0218 | 5.1299 | 5.2367 | 5.3424 | 5.4471 | 5.5509 | 5.7562 | 5.959 | 6.1597 | 6.3589 | 6.5571
216 | M | Lmax |  | 6.7026 | m | [7 empty] | 4.9152 | 5.3621 | 5.8089 | 6.2558 | 6.7026 | 7.1494 | 7.5963 | 8.0431 | 8.49 | 8.9368 | 9.3836 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595
(4-row) | Medium | Wmin |  | 3.8392 | m | [7 empty] | 3.2765 | 3.4248 | 3.5675 | 3.7055 | 3.8392 | 3.9691 | 4.0957 | 4.2193 | 4.3402 | 4.4586 | 4.5749 | 4.6892 | 4.8016 | 4.9125 | 5.0218 | 5.1299 | 5.2367 | 5.3424 | 5.4471 | 5.5509 | 5.7562 | 5.959 | 6.1597 | 6.3589 | 6.5571
|  | Wmax |  | 6.7026 | m | [7 empty] | 4.9152 | 5.3621 | 5.8089 | 6.2558 | 6.7026 | 7.1494 | 7.5963 | 8.0431 | 8.49 | 8.9368 | 9.3836 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595
|  | L Vsp.min |  | 5.0117 | [8 empty] | 4.2772 | 4.4707 | 4.6571 | 4.8371 | 5.0117 | 5.1813 | 5.3465 | 5.5078 | 5.6656 | 5.8203 | 5.972 | 6.1212 | 6.268 | 6.4127 | 6.5555 | 6.6965 | 6.836 | 6.974 | 7.1107 | 7.2462 | 7.5142 | 7.7788 | 8.0409 | 8.3009 | 8.5596
|  | L Vsp.max |  | 9.6104 | [8 empty] | 7.9068 | 8.3327 | 8.7573 | 9.1826 | 9.6104 | 10.0424 | 10.4798 | 10.9239 | 11.3759 | 11.8368 | 12.3075 | 12.7889 | 13.2819 | 13.787 | 14.3052 | 14.8371 | 15.3832 | 15.9443 | 16.5209 | 17.1136 | 18.3492 | 19.6553 | 21.0358 | 22.494 | 24.0336
|  | L throw max |  | 8.7496 | [8 empty] | 6.4164 | 6.9997 | 7.583 | 8.1663 | 8.7496 | 9.3329 | 9.9162 | 10.4995 | 11.0828 | 11.6661 | 12.2494 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485
|  | W Vsp.min |  | 2.9043 | [8 empty] | 2.4787 | 2.5908 | 2.6988 | 2.8032 | 2.9043 | 3.0026 | 3.0984 | 3.1918 | 3.2833 | 3.3729 | 3.4608 | 3.5473 | 3.6324 | 3.7162 | 3.799 | 3.8807 | 3.9615 | 4.0415 | 4.1207 | 4.1992 | 4.3545 | 4.5079 | 4.6597 | 4.8105 | 4.9603
|  | W Vsp.max |  | 5.5693 | [8 empty] | 4.5821 | 4.8289 | 5.0749 | 5.3214 | 5.5693 | 5.8196 | 6.0731 | 6.3305 | 6.5924 | 6.8595 | 7.1323 | 7.4113 | 7.6969 | 7.9897 | 8.29 | 8.5982 | 8.9147 | 9.2399 | 9.574 | 9.9175 | 10.6335 | 11.3904 | 12.1904 | 13.0355 | 13.9277
|  | W throw max |  | 5.0705 | [8 empty] | 3.7183 | 4.0564 | 4.3944 | 4.7324 | 5.0705 | 5.4085 | 5.7465 | 6.0845 | 6.4226 | 6.7606 | 7.0986 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561
|  | Lmin |  | 5.0117 | m | [7 empty] | 4.2772 | 4.4707 | 4.6571 | 4.8371 | 5.0117 | 5.1813 | 5.3465 | 5.5078 | 5.6656 | 5.8203 | 5.972 | 6.1212 | 6.268 | 6.4127 | 6.5555 | 6.6965 | 6.836 | 6.974 | 7.1107 | 7.2462 | 7.5142 | 7.7788 | 8.0409 | 8.3009 | 8.5596
| L | Lmax |  | 8.7496 | m | [7 empty] | 6.4164 | 6.9997 | 7.583 | 8.1663 | 8.7496 | 9.3329 | 9.9162 | 10.4995 | 11.0828 | 11.6661 | 12.2494 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485
| Long | Wmin |  | 2.9043 | m | [7 empty] | 2.4787 | 2.5908 | 2.6988 | 2.8032 | 2.9043 | 3.0026 | 3.0984 | 3.1918 | 3.2833 | 3.3729 | 3.4608 | 3.5473 | 3.6324 | 3.7162 | 3.799 | 3.8807 | 3.9615 | 4.0415 | 4.1207 | 4.1992 | 4.3545 | 4.5079 | 4.6597 | 4.8105 | 4.9603
|  | Wmax |  | 5.0705 | m | [7 empty] | 3.7183 | 4.0564 | 4.3944 | 4.7324 | 5.0705 | 5.4085 | 5.7465 | 6.0845 | 6.4226 | 6.7606 | 7.0986 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561
[7 empty] | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240 | 250 | 260 | 270 | 280 | 290 | 300 | 320 | 340 | 360 | 380 | 400

## DN 1500 (hidden)
| FACTORS: | K.l.min |  | 7
|  | K.l.max |  | 21
|  | K.dT |  | 1 | -12 K / dT
|  | K.H.min(sp) |  | 1.0037 | Increased draught risk as height increases, Fig 8, Krantz Layout Criteria TB 69 E
|  | K.H.max(vol) |  | 1 | Reduce max throw with height to maintain constant volume to prevent stagnation
|  | K.2D/3D |  | 1.1597 | Fig 8 / Fig 7 @ 0.25, Krantz Layout Criteria TB 69 E
|  | K.adpi |  | 0.94595 | Adjustment factor for ADPI
|  | v.room ≤ |  | 0.23665 | m/s, Krantz Layout Criteria TB 69 E
|  | K.h.min |  | 1.9
INPUT
|  |  | H.diffuser = | 2.5 | m | Height to Diffuser Centre-Line = 2.0 to 4.5 m
PMW- | L.neck |  | dT(cooling) = | -12 | K | dT = -8 K to -12 K
AD- | mm | ADPI ≥ 90% | ADPI ³ | 90 | % | 70%, 80%, 90% or 95%
DN 1500 | 1455 | = |  | 200 | L/s |  | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240 | 250 | 260 | 270 | 280 | 290 | 300 | 320 | 340 | 360 | 380 | 400 | 420 | 440 | 460 | 480 | 500 | 520 | 540 | 560 | 580 | 600
|  | Pt |  | 22.7574 | Pa |  | 4.4986 | 5.5715 | 6.761 | 8.0673 | 9.4907 | 11.0317 | 12.6903 | 14.4669 | 16.3617 | 18.375 | 20.5068 | 22.7574 | 25.1271 | 27.6159 | 30.224 | 32.9516 | 35.7989 | 38.766 | 41.853 | 45.0601 | 48.3874 | [11 empty] | ≤ 20 | ≤ 30 | ≤ 40 | ≤ 50 | Pa
H.neck | Throw | Lw |  | 41.4724 | dB(A) |  | 15.9122 | 19.2848 | 22.3356 | 25.1209 | 27.683 | 30.0552 | 32.2637 | 34.3296 | 36.2702 | 38.0998 | 39.8305 | 41.4724 | 43.0342 | 44.5233 | 45.9462 | 47.3085 | 48.6152 | 49.8707 | 51.0787 | 52.2429 | 53.3661 | [11 empty] | ≤ 40 | ≤ 45 | ≤ 50 | ≤ 55 | dB(A)
mm | Setting | Lp* |  | 26.4724 | NC* |  | <5 | <5 | 7.3356 | 10.1209 | 12.683 | 15.0552 | 17.2637 | 19.3296 | 21.2702 | 23.0998 | 24.8305 | 26.4724 | 28.0342 | 29.5233 | 30.9462 | 32.3085 | 33.6152 | 34.8707 | 36.0787 | 37.2429 | 38.3661 | [11 empty] | ≤ 25 | ≤ 30 | ≤ 35 | ≤ 40 | NC*
|  | L Vsp.min |  | 3.4281 |  |  | 2.2464 | 2.3707 | 2.4896 | 2.604 | 2.7146 | 2.8217 | 2.926 | 3.0278 | 3.1273 | 3.225 | 3.3209 | 3.4154 | 3.5086 | 3.6007 | 3.6918 | 3.7821 | 3.8717 | 3.9607 | 4.0493 | 4.1374 | 4.2253
|  | L Vsp.max |  | 7.7683 |  |  | 4.2153 | 4.505 | 4.7966 | 5.0922 | 5.3934 | 5.7018 | 6.0188 | 6.3453 | 6.6827 | 7.0317 | 7.3933 | 7.7683 | 8.1576 | 8.5618 | 8.9816 | 9.4177 | 9.8707 | 10.3412 | 10.8298 | 11.3371 | 11.8635
|  | L throw max |  | 7.1895 |  |  | 3.5802 | 3.978 | 4.3758 | 4.7736 | 5.1714 | 5.5692 | 5.967 | 6.3649 | 6.5058 | 6.5502 | 6.5945 | 6.6389 | 6.6833 | 6.7276 | 6.772 | 6.8163 | 6.8607 | 6.9051 | 6.9494 | 6.9938 | 7.0382
|  | W Vsp.min |  | 5.9399 |  |  | 3.8923 | 4.1077 | 4.3137 | 4.512 | 4.7035 | 4.8891 | 5.0698 | 5.2461 | 5.4186 | 5.5878 | 5.7541 | 5.9178 | 6.0792 | 6.2388 | 6.3967 | 6.5532 | 6.7084 | 6.8626 | 7.016 | 7.1688 | 7.321
|  | W Vsp.max |  | 13.46 |  |  | 7.3038 | 7.8058 | 8.311 | 8.8231 | 9.3451 | 9.8794 | 10.4285 | 10.9944 | 11.5789 | 12.1836 | 12.8102 | 13.46 | 14.1344 | 14.8348 | 15.5622 | 16.3178 | 17.1027 | 17.918 | 18.7646 | 19.6435 | 20.5556
|  | W throw max |  | 12.457 |  |  | 6.2034 | 6.8926 | 7.5819 | 8.2712 | 8.9604 | 9.6497 | 10.3389 | 11.0282 | 11.2724 | 11.3493 | 11.4262 | 11.503 | 11.5799 | 11.6568 | 11.7336 | 11.8105 | 11.8874 | 11.9642 | 12.0411 | 12.118 | 12.1949
|  | Hmin |  | 2.3085 | m |  | 2.1388 | 2.1543 | 2.1697 | 2.1851 | 2.2006 | 2.216 | 2.2314 | 2.2468 | 2.2623 | 2.2777 | 2.2931 | 2.3085 | 2.324 | 2.3394 | 2.3548 | 2.3702 | 2.3857 | 2.4011 | 2.4165 | 2.432 | 2.4474 | [11 empty] | * for 10 dB room absorption
|  | Lmin |  | 3.4281 | m |  | 2.2464 | 2.3707 | 2.4896 | 2.604 | 2.7146 | 2.8217 | 2.926 | 3.0278 | 3.1273 | 3.225 | 3.3209 | 3.4154 | 3.5086 | 3.6007 | 3.6918 | 3.7821 | 3.8717 | 3.9607 | 4.0493 | 4.1374 | 4.2253
| S | Lmax |  | 7.1895 | m |  | 3.5802 | 3.978 | 4.3758 | 4.7736 | 5.1714 | 5.5692 | 5.967 | 6.3453 | 6.5058 | 6.5502 | 6.5945 | 6.6389 | 6.6833 | 6.7276 | 6.772 | 6.8163 | 6.8607 | 6.9051 | 6.9494 | 6.9938 | 7.0382
| Short | Wmin |  | 5.9399 | m |  | 3.8923 | 4.1077 | 4.3137 | 4.512 | 4.7035 | 4.8891 | 5.0698 | 5.2461 | 5.4186 | 5.5878 | 5.7541 | 5.9178 | 6.0792 | 6.2388 | 6.3967 | 6.5532 | 6.7084 | 6.8626 | 7.016 | 7.1688 | 7.321
|  | Wmax |  | 12.457 | m |  | 6.2034 | 6.8926 | 7.5819 | 8.2712 | 8.9604 | 9.6497 | 10.3389 | 10.9944 | 11.2724 | 11.3493 | 11.4262 | 11.503 | 11.5799 | 11.6568 | 11.7336 | 11.8105 | 11.8874 | 11.9642 | 12.0411 | 12.118 | 12.1949
|  | L,W Vsp.min |  | 4.5106 |  |  | 2.9557 | 3.1193 | 3.2757 | 3.4263 | 3.5717 | 3.7127 | 3.8499 | 3.9838 | 4.1148 | 4.2432 | 4.3695 | 4.4938 | 4.6164 | 4.7376 | 4.8575 | 4.9763 | 5.0942 | 5.2113 | 5.3278 | 5.4438 | 5.5594
|  | L,W Vsp.max |  | 10.2212 |  |  | 5.5463 | 5.9275 | 6.3112 | 6.7 | 7.0964 | 7.5022 | 7.9192 | 8.3489 | 8.7927 | 9.2519 | 9.7277 | 10.2212 | 10.7333 | 11.2651 | 11.8175 | 12.3913 | 12.9874 | 13.6064 | 14.2493 | 14.9167 | 15.6094
|  | L,W throw max |  | 9.4595 |  |  | 4.7107 | 5.2341 | 5.7575 | 6.2809 | 6.8043 | 7.3277 | 7.8511 | 8.3745 | 8.56 | 8.6183 | 8.6767 | 8.7351 | 8.7935 | 8.8518 | 8.9102 | 8.9686 | 9.027 | 9.0853 | 9.1437 | 9.2021 | 9.2604
|  | Lmin |  | 4.5106 | m |  | 2.9557 | 3.1193 | 3.2757 | 3.4263 | 3.5717 | 3.7127 | 3.8499 | 3.9838 | 4.1148 | 4.2432 | 4.3695 | 4.4938 | 4.6164 | 4.7376 | 4.8575 | 4.9763 | 5.0942 | 5.2113 | 5.3278 | 5.4438 | 5.5594
99 | M | Lmax |  | 9.4595 | m |  | 4.7107 | 5.2341 | 5.7575 | 6.2809 | 6.8043 | 7.3277 | 7.8511 | 8.3489 | 8.56 | 8.6183 | 8.6767 | 8.7351 | 8.7935 | 8.8518 | 8.9102 | 8.9686 | 9.027 | 9.0853 | 9.1437 | 9.2021 | 9.2604
(1-row) | Medium | Wmin |  | 4.5106 | m |  | 2.9557 | 3.1193 | 3.2757 | 3.4263 | 3.5717 | 3.7127 | 3.8499 | 3.9838 | 4.1148 | 4.2432 | 4.3695 | 4.4938 | 4.6164 | 4.7376 | 4.8575 | 4.9763 | 5.0942 | 5.2113 | 5.3278 | 5.4438 | 5.5594
|  | Wmax |  | 9.4595 | m |  | 4.7107 | 5.2341 | 5.7575 | 6.2809 | 6.8043 | 7.3277 | 7.8511 | 8.3489 | 8.56 | 8.6183 | 8.6767 | 8.7351 | 8.7935 | 8.8518 | 8.9102 | 8.9686 | 9.027 | 9.0853 | 9.1437 | 9.2021 | 9.2604
|  | L Vsp.min |  | 5.8881 |  |  | 3.8584 | 4.0719 | 4.2762 | 4.4726 | 4.6625 | 4.8465 | 5.0257 | 5.2004 | 5.3714 | 5.5391 | 5.7039 | 5.8662 | 6.0263 | 6.1844 | 6.341 | 6.4961 | 6.65 | 6.8028 | 6.9549 | 7.1063 | 7.2572
|  | L Vsp.max |  | 13.3427 |  |  | 7.2402 | 7.7377 | 8.2386 | 8.7462 | 9.2636 | 9.7934 | 10.3377 | 10.8986 | 11.478 | 12.0774 | 12.6985 | 13.3427 | 14.0113 | 14.7055 | 15.4266 | 16.1756 | 16.9537 | 17.7619 | 18.6011 | 19.4723 | 20.3765
|  | L throw max |  | 12.3485 |  |  | 6.1493 | 6.8326 | 7.5158 | 8.1991 | 8.8823 | 9.5656 | 10.2489 | 10.9321 | 11.1742 | 11.2504 | 11.3266 | 11.4028 | 11.479 | 11.5552 | 11.6314 | 11.7076 | 11.7838 | 11.86 | 11.9362 | 12.0124 | 12.0886
|  | W Vsp.min |  | 3.4122 |  |  | 2.236 | 2.3597 | 2.4781 | 2.5919 | 2.7019 | 2.8086 | 2.9124 | 3.0137 | 3.1128 | 3.21 | 3.3055 | 3.3995 | 3.4923 | 3.5839 | 3.6746 | 3.7645 | 3.8537 | 3.9423 | 4.0304 | 4.1182 | 4.2056
|  | W Vsp.max |  | 7.7322 |  |  | 4.1957 | 4.4841 | 4.7743 | 5.0685 | 5.3683 | 5.6753 | 5.9908 | 6.3158 | 6.6516 | 6.999 | 7.3589 | 7.7322 | 8.1197 | 8.522 | 8.9398 | 9.3739 | 9.8248 | 10.2931 | 10.7795 | 11.2844 | 11.8083
|  | W throw max |  | 7.1561 |  |  | 3.5636 | 3.9595 | 4.3555 | 4.7514 | 5.1474 | 5.5433 | 5.9393 | 6.3352 | 6.4755 | 6.5197 | 6.5639 | 6.608 | 6.6522 | 6.6963 | 6.7405 | 6.7846 | 6.8288 | 6.873 | 6.9171 | 6.9613 | 7.0054
|  | Lmin |  | 5.8881 | m |  | 3.8584 | 4.0719 | 4.2762 | 4.4726 | 4.6625 | 4.8465 | 5.0257 | 5.2004 | 5.3714 | 5.5391 | 5.7039 | 5.8662 | 6.0263 | 6.1844 | 6.341 | 6.4961 | 6.65 | 6.8028 | 6.9549 | 7.1063 | 7.2572
| L | Lmax |  | 12.3485 | m |  | 6.1493 | 6.8326 | 7.5158 | 8.1991 | 8.8823 | 9.5656 | 10.2489 | 10.8986 | 11.1742 | 11.2504 | 11.3266 | 11.4028 | 11.479 | 11.5552 | 11.6314 | 11.7076 | 11.7838 | 11.86 | 11.9362 | 12.0124 | 12.0886
| Long | Wmin |  | 3.4122 | m |  | 2.236 | 2.3597 | 2.4781 | 2.5919 | 2.7019 | 2.8086 | 2.9124 | 3.0137 | 3.1128 | 3.21 | 3.3055 | 3.3995 | 3.4923 | 3.5839 | 3.6746 | 3.7645 | 3.8537 | 3.9423 | 4.0304 | 4.1182 | 4.2056
|  | Wmax |  | 7.1561 | m |  | 3.5636 | 3.9595 | 4.3555 | 4.7514 | 5.1474 | 5.5433 | 5.9393 | 6.3158 | 6.4755 | 6.5197 | 6.5639 | 6.608 | 6.6522 | 6.6963 | 6.7405 | 6.7846 | 6.8288 | 6.873 | 6.9171 | 6.9613 | 7.0054
|  | Pt |  | 11.5952 | Pa |  |  |  |  | 4.1104 | 4.8357 | 5.6208 | 6.4659 | 7.3711 | 8.3365 | 9.3623 | 10.4485 | 11.5952 | 12.8026 | 14.0707 | 15.3996 | 16.7893 | 18.2401 | 19.7518 | 21.3247 | 22.9588 | 24.6541 | 26.4107 | 30.1081 | 34.0515 | 38.2414 | 42.6781 | 47.3621
H.neck | Throw | Lw |  | 32.2832 | dB(A) |  |  |  |  | 15.9317 | 18.4939 | 20.8661 | 23.0745 | 25.1404 | 27.081 | 28.9106 | 30.6413 | 32.2832 | 33.845 | 35.3341 | 36.757 | 38.1193 | 39.4261 | 40.6815 | 41.8896 | 43.0537 | 44.177 | 45.2622 | 47.328 | 49.2686 | 51.0983 | 52.829 | 54.4709
mm | Setting | Lp* |  | 17.2832 | NC* |  |  |  |  | <5 | <5 | 5.8661 | 8.0745 | 10.1404 | 12.081 | 13.9106 | 15.6413 | 17.2832 | 18.845 | 20.3341 | 21.757 | 23.1193 | 24.4261 | 25.6815 | 26.8896 | 28.0537 | 29.177 | 30.2622 | 32.328 | 34.2686 | 36.0983 | 37.829 | 39.4709
|  | L Vsp.min |  | 3.3873 | [5 empty] | 2.5929 | 2.7009 | 2.8052 | 2.9064 | 3.0046 | 3.1003 | 3.1938 | 3.2852 | 3.3747 | 3.4625 | 3.5489 | 3.6338 | 3.7175 | 3.8001 | 3.8816 | 3.9623 | 4.042 | 4.121 | 4.1993 | 4.3541 | 4.5068 | 4.658 | 4.808 | 4.957
|  | L Vsp.max |  | 6.8608 | [5 empty] | 4.843 | 5.0883 | 5.3338 | 5.5805 | 5.8293 | 6.0811 | 6.3365 | 6.5962 | 6.8608 | 7.1308 | 7.4068 | 7.6891 | 7.9783 | 8.2746 | 8.5787 | 8.8907 | 9.211 | 9.54 | 9.878 | 10.5822 | 11.3259 | 12.1113 | 12.9404 | 13.8151
|  | L throw max |  | 7.1895 | [5 empty] | 4.7736 | 5.1714 | 5.5692 | 5.967 | 6.3649 | 6.5058 | 6.5502 | 6.5945 | 6.6389 | 6.6833 | 6.7276 | 6.772 | 6.8163 | 6.8607 | 6.9051 | 6.9494 | 6.9938 | 7.0382 | 7.0825 | 7.1713 | 7.26 | 7.3487 | 7.4375 | 7.5262
|  | W Vsp.min |  | 5.869 | [5 empty] | 4.4926 | 4.6797 | 4.8605 | 5.0358 | 5.206 | 5.3719 | 5.5338 | 5.6921 | 5.8472 | 5.9994 | 6.149 | 6.2962 | 6.4413 | 6.5843 | 6.7256 | 6.8653 | 7.0035 | 7.1404 | 7.276 | 7.5442 | 7.8089 | 8.0708 | 8.3306 | 8.5889
|  | W Vsp.max |  | 11.8876 | [5 empty] | 8.3914 | 8.8164 | 9.2417 | 9.6692 | 10.1003 | 10.5366 | 10.9791 | 11.4291 | 11.8876 | 12.3554 | 12.8335 | 13.3227 | 13.8237 | 14.3373 | 14.864 | 15.4046 | 15.9596 | 16.5297 | 17.1154 | 18.3355 | 19.6241 | 20.9849 | 22.4214 | 23.937
|  | W throw max |  | 12.457 | [5 empty] | 8.2712 | 8.9604 | 9.6497 | 10.3389 | 11.0282 | 11.2724 | 11.3493 | 11.4262 | 11.503 | 11.5799 | 11.6568 | 11.7336 | 11.8105 | 11.8874 | 11.9642 | 12.0411 | 12.118 | 12.1949 | 12.2717 | 12.4255 | 12.5792 | 12.7329 | 12.8867 | 13.0404
|  | Hmin |  | 2.3085 | m |  |  |  |  | 2.1851 | 2.2006 | 2.216 | 2.2314 | 2.2468 | 2.2623 | 2.2777 | 2.2931 | 2.3085 | 2.324 | 2.3394 | 2.3548 | 2.3702 | 2.3857 | 2.4011 | 2.4165 | 2.432 | 2.4474 | 2.4628 | 2.4937 | 2.5245 | 2.5554 | 2.5862 | 2.6171
|  | Lmin |  | 3.3873 | m |  |  |  |  | 2.5929 | 2.7009 | 2.8052 | 2.9064 | 3.0046 | 3.1003 | 3.1938 | 3.2852 | 3.3747 | 3.4625 | 3.5489 | 3.6338 | 3.7175 | 3.8001 | 3.8816 | 3.9623 | 4.042 | 4.121 | 4.1993 | 4.3541 | 4.5068 | 4.658 | 4.808 | 4.957
| S | Lmax |  | 6.8608 | m |  |  |  |  | 4.7736 | 5.0883 | 5.3338 | 5.5805 | 5.8293 | 6.0811 | 6.3365 | 6.5945 | 6.6389 | 6.6833 | 6.7276 | 6.772 | 6.8163 | 6.8607 | 6.9051 | 6.9494 | 6.9938 | 7.0382 | 7.0825 | 7.1713 | 7.26 | 7.3487 | 7.4375 | 7.5262
| Short | Wmin |  | 5.869 | m |  |  |  |  | 4.4926 | 4.6797 | 4.8605 | 5.0358 | 5.206 | 5.3719 | 5.5338 | 5.6921 | 5.8472 | 5.9994 | 6.149 | 6.2962 | 6.4413 | 6.5843 | 6.7256 | 6.8653 | 7.0035 | 7.1404 | 7.276 | 7.5442 | 7.8089 | 8.0708 | 8.3306 | 8.5889
|  | Wmax |  | 11.8876 | m |  |  |  |  | 8.2712 | 8.8164 | 9.2417 | 9.6692 | 10.1003 | 10.5366 | 10.9791 | 11.4262 | 11.503 | 11.5799 | 11.6568 | 11.7336 | 11.8105 | 11.8874 | 11.9642 | 12.0411 | 12.118 | 12.1949 | 12.2717 | 12.4255 | 12.5792 | 12.7329 | 12.8867 | 13.0404
|  | L,W Vsp.min |  | 4.4568 | [5 empty] | 3.4116 | 3.5537 | 3.691 | 3.824 | 3.9533 | 4.0793 | 4.2022 | 4.3224 | 4.4402 | 4.5558 | 4.6694 | 4.7812 | 4.8913 | 5 | 5.1073 | 5.2133 | 5.3183 | 5.4222 | 5.5252 | 5.7289 | 5.9299 | 6.1288 | 6.3261 | 6.5222
|  | L,W Vsp.max |  | 9.0271 | [5 empty] | 6.3722 | 6.6949 | 7.0179 | 7.3425 | 7.6699 | 8.0012 | 8.3373 | 8.679 | 9.0271 | 9.3824 | 9.7454 | 10.1169 | 10.4974 | 10.8873 | 11.2873 | 11.6978 | 12.1193 | 12.5522 | 12.9969 | 13.9235 | 14.902 | 15.9354 | 17.0262 | 18.1771
|  | L,W throw max |  | 9.4595 | [5 empty] | 6.2809 | 6.8043 | 7.3277 | 7.8511 | 8.3745 | 8.56 | 8.6183 | 8.6767 | 8.7351 | 8.7935 | 8.8518 | 8.9102 | 8.9686 | 9.027 | 9.0853 | 9.1437 | 9.2021 | 9.2604 | 9.3188 | 9.4356 | 9.5523 | 9.6691 | 9.7858 | 9.9025
|  | Lmin |  | 4.4568 | m |  |  |  |  | 3.4116 | 3.5537 | 3.691 | 3.824 | 3.9533 | 4.0793 | 4.2022 | 4.3224 | 4.4402 | 4.5558 | 4.6694 | 4.7812 | 4.8913 | 5 | 5.1073 | 5.2133 | 5.3183 | 5.4222 | 5.5252 | 5.7289 | 5.9299 | 6.1288 | 6.3261 | 6.5222
138 | M | Lmax |  | 9.0271 | m |  |  |  |  | 6.2809 | 6.6949 | 7.0179 | 7.3425 | 7.6699 | 8.0012 | 8.3373 | 8.6767 | 8.7351 | 8.7935 | 8.8518 | 8.9102 | 8.9686 | 9.027 | 9.0853 | 9.1437 | 9.2021 | 9.2604 | 9.3188 | 9.4356 | 9.5523 | 9.6691 | 9.7858 | 9.9025
(2-row) | Medium | Wmin |  | 4.4568 | m |  |  |  |  | 3.4116 | 3.5537 | 3.691 | 3.824 | 3.9533 | 4.0793 | 4.2022 | 4.3224 | 4.4402 | 4.5558 | 4.6694 | 4.7812 | 4.8913 | 5 | 5.1073 | 5.2133 | 5.3183 | 5.4222 | 5.5252 | 5.7289 | 5.9299 | 6.1288 | 6.3261 | 6.5222
|  | Wmax |  | 9.0271 | m |  |  |  |  | 6.2809 | 6.6949 | 7.0179 | 7.3425 | 7.6699 | 8.0012 | 8.3373 | 8.6767 | 8.7351 | 8.7935 | 8.8518 | 8.9102 | 8.9686 | 9.027 | 9.0853 | 9.1437 | 9.2021 | 9.2604 | 9.3188 | 9.4356 | 9.5523 | 9.6691 | 9.7858 | 9.9025
|  | L Vsp.min |  | 5.8179 | [5 empty] | 4.4534 | 4.639 | 4.8182 | 4.9919 | 5.1607 | 5.3251 | 5.4855 | 5.6425 | 5.7963 | 5.9472 | 6.0954 | 6.2414 | 6.3851 | 6.527 | 6.667 | 6.8055 | 6.9425 | 7.0781 | 7.2126 | 7.4785 | 7.7408 | 8.0005 | 8.258 | 8.5141
|  | L Vsp.max |  | 11.784 | [5 empty] | 8.3182 | 8.7395 | 9.1612 | 9.5849 | 10.0123 | 10.4448 | 10.8835 | 11.3295 | 11.784 | 12.2478 | 12.7217 | 13.2066 | 13.7033 | 14.2123 | 14.7345 | 15.2704 | 15.8206 | 16.3857 | 16.9662 | 18.1757 | 19.4531 | 20.802 | 22.226 | 23.7284
|  | L throw max |  | 12.3485 | [5 empty] | 8.1991 | 8.8823 | 9.5656 | 10.2489 | 10.9321 | 11.1742 | 11.2504 | 11.3266 | 11.4028 | 11.479 | 11.5552 | 11.6314 | 11.7076 | 11.7838 | 11.86 | 11.9362 | 12.0124 | 12.0886 | 12.1648 | 12.3172 | 12.4696 | 12.622 | 12.7744 | 12.9268
|  | W Vsp.min |  | 3.3715 | [5 empty] | 2.5808 | 2.6883 | 2.7922 | 2.8928 | 2.9906 | 3.0859 | 3.1789 | 3.2699 | 3.359 | 3.4464 | 3.5324 | 3.6169 | 3.7002 | 3.7824 | 3.8636 | 3.9438 | 4.0232 | 4.1018 | 4.1798 | 4.3338 | 4.4859 | 4.6363 | 4.7856 | 4.934
|  | W Vsp.max |  | 6.8289 | [5 empty] | 4.8205 | 5.0646 | 5.309 | 5.5545 | 5.8022 | 6.0528 | 6.3071 | 6.5656 | 6.8289 | 7.0977 | 7.3723 | 7.6533 | 7.9412 | 8.2362 | 8.5388 | 8.8493 | 9.1681 | 9.4956 | 9.8321 | 10.533 | 11.2732 | 12.0549 | 12.8802 | 13.7508
|  | W throw max |  | 7.1561 | [5 empty] | 4.7514 | 5.1474 | 5.5433 | 5.9393 | 6.3352 | 6.4755 | 6.5197 | 6.5639 | 6.608 | 6.6522 | 6.6963 | 6.7405 | 6.7846 | 6.8288 | 6.873 | 6.9171 | 6.9613 | 7.0054 | 7.0496 | 7.1379 | 7.2262 | 7.3145 | 7.4029 | 7.4912
|  | Lmin |  | 5.8179 | m |  |  |  |  | 4.4534 | 4.639 | 4.8182 | 4.9919 | 5.1607 | 5.3251 | 5.4855 | 5.6425 | 5.7963 | 5.9472 | 6.0954 | 6.2414 | 6.3851 | 6.527 | 6.667 | 6.8055 | 6.9425 | 7.0781 | 7.2126 | 7.4785 | 7.7408 | 8.0005 | 8.258 | 8.5141
| L | Lmax |  | 11.784 | m |  |  |  |  | 8.1991 | 8.7395 | 9.1612 | 9.5849 | 10.0123 | 10.4448 | 10.8835 | 11.3266 | 11.4028 | 11.479 | 11.5552 | 11.6314 | 11.7076 | 11.7838 | 11.86 | 11.9362 | 12.0124 | 12.0886 | 12.1648 | 12.3172 | 12.4696 | 12.622 | 12.7744 | 12.9268
| Long | Wmin |  | 3.3715 | m |  |  |  |  | 2.5808 | 2.6883 | 2.7922 | 2.8928 | 2.9906 | 3.0859 | 3.1789 | 3.2699 | 3.359 | 3.4464 | 3.5324 | 3.6169 | 3.7002 | 3.7824 | 3.8636 | 3.9438 | 4.0232 | 4.1018 | 4.1798 | 4.3338 | 4.4859 | 4.6363 | 4.7856 | 4.934
|  | Wmax |  | 6.8289 | m |  |  |  |  | 4.7514 | 5.0646 | 5.309 | 5.5545 | 5.8022 | 6.0528 | 6.3071 | 6.5639 | 6.608 | 6.6522 | 6.6963 | 6.7405 | 6.7846 | 6.8288 | 6.873 | 6.9171 | 6.9613 | 7.0054 | 7.0496 | 7.1379 | 7.2262 | 7.3145 | 7.4029 | 7.4912
|  | Pt |  | 6.9956 | Pa | [8 empty] | 4.4471 | 5.0296 | 5.6485 | 6.3038 | 6.9956 | 7.7241 | 8.4891 | 9.2908 | 10.1293 | 11.0046 | 11.9167 | 12.8656 | 13.8515 | 14.8743 | 15.9341 | 18.1648 | 20.544 | 23.0718 | 25.7485 | 28.5744 | 31.5498 | 34.6747 | 37.9495 | 41.3744 | 44.9495
H.neck | Throw | Lw |  | 25.397 | dB(A) | [8 empty] | 18.2542 | 20.1948 | 22.0244 | 23.7551 | 25.397 | 26.9588 | 28.4479 | 29.8708 | 31.2331 | 32.5398 | 33.7953 | 35.0034 | 36.1675 | 37.2908 | 38.3759 | 40.4418 | 42.3824 | 44.2121 | 45.9428 | 47.5847 | 49.1464 | 50.6355 | 52.0584 | 53.4208 | 54.7275
mm | Setting | Lp* |  | 10.397 | NC* | [8 empty] | <5 | 5.1948 | 7.0244 | 8.7551 | 10.397 | 11.9588 | 13.4479 | 14.8708 | 16.2331 | 17.5398 | 18.7953 | 20.0034 | 21.1675 | 22.2908 | 23.3759 | 25.4418 | 27.3824 | 29.2121 | 30.9428 | 32.5847 | 34.1464 | 35.6355 | 37.0584 | 38.4208 | 39.7275
|  | L Vsp.min |  | 3.3704 | [9 empty] | 2.9951 | 3.0892 | 3.1809 | 3.2704 | 3.3579 | 3.4435 | 3.5275 | 3.6099 | 3.6909 | 3.7706 | 3.8491 | 3.9264 | 4.0027 | 4.0781 | 4.1525 | 4.299 | 4.4426 | 4.5838 | 4.7228 | 4.8601 | 4.9959 | 5.1303 | 5.2637 | 5.3963 | 5.5282
|  | L Vsp.max |  | 6.4869 | [9 empty] | 5.6167 | 5.8332 | 6.0501 | 6.2678 | 6.4869 | 6.7078 | 6.9308 | 7.1565 | 7.3851 | 7.617 | 7.8523 | 8.0916 | 8.3349 | 8.5826 | 8.8348 | 9.354 | 9.894 | 10.4566 | 11.0431 | 11.6549 | 12.2933 | 12.9594 | 13.6545 | 14.3795 | 15.1356
|  | L throw max |  | 7.1895 | [9 empty] | 6.3649 | 6.5058 | 6.5502 | 6.5945 | 6.6389 | 6.6833 | 6.7276 | 6.772 | 6.8163 | 6.8607 | 6.9051 | 6.9494 | 6.9938 | 7.0382 | 7.0825 | 7.1713 | 7.26 | 7.3487 | 7.4375 | 7.5262 | 7.6149 | 7.7036 | 7.7924 | 7.8811 | 7.9698
|  | W Vsp.min |  | 5.8399 | [9 empty] | 5.1895 | 5.3526 | 5.5115 | 5.6666 | 5.8181 | 5.9665 | 6.112 | 6.2548 | 6.3952 | 6.5332 | 6.6692 | 6.8032 | 6.9354 | 7.0659 | 7.1949 | 7.4487 | 7.6976 | 7.9422 | 8.1831 | 8.421 | 8.6562 | 8.8892 | 9.1203 | 9.35 | 9.5786
|  | W Vsp.max |  | 11.2396 | [9 empty] | 9.7319 | 10.1071 | 10.4828 | 10.86 | 11.2396 | 11.6223 | 12.0089 | 12.3999 | 12.796 | 13.1977 | 13.6056 | 14.02 | 14.4416 | 14.8708 | 15.3078 | 16.2073 | 17.1431 | 18.1179 | 19.1341 | 20.1942 | 21.3002 | 22.4544 | 23.6587 | 24.915 | 26.225
|  | W throw max |  | 12.457 | [9 empty] | 11.0282 | 11.2724 | 11.3493 | 11.4262 | 11.503 | 11.5799 | 11.6568 | 11.7336 | 11.8105 | 11.8874 | 11.9642 | 12.0411 | 12.118 | 12.1949 | 12.2717 | 12.4255 | 12.5792 | 12.7329 | 12.8867 | 13.0404 | 13.1942 | 13.3479 | 13.5016 | 13.6554 | 13.8091
|  | Hmin |  | 2.3085 | m | [8 empty] | 2.2468 | 2.2623 | 2.2777 | 2.2931 | 2.3085 | 2.324 | 2.3394 | 2.3548 | 2.3702 | 2.3857 | 2.4011 | 2.4165 | 2.432 | 2.4474 | 2.4628 | 2.4937 | 2.5245 | 2.5554 | 2.5862 | 2.6171 | 2.6479 | 2.6788 | 2.7096 | 2.7405 | 2.7713
|  | Lmin |  | 3.3704 | m | [8 empty] | 2.9951 | 3.0892 | 3.1809 | 3.2704 | 3.3579 | 3.4435 | 3.5275 | 3.6099 | 3.6909 | 3.7706 | 3.8491 | 3.9264 | 4.0027 | 4.0781 | 4.1525 | 4.299 | 4.4426 | 4.5838 | 4.7228 | 4.8601 | 4.9959 | 5.1303 | 5.2637 | 5.3963 | 5.5282
| S | Lmax |  | 6.4869 | m | [8 empty] | 5.6167 | 5.8332 | 6.0501 | 6.2678 | 6.4869 | 6.6833 | 6.7276 | 6.772 | 6.8163 | 6.8607 | 6.9051 | 6.9494 | 6.9938 | 7.0382 | 7.0825 | 7.1713 | 7.26 | 7.3487 | 7.4375 | 7.5262 | 7.6149 | 7.7036 | 7.7924 | 7.8811 | 7.9698
| Short | Wmin |  | 5.8399 | m | [8 empty] | 5.1895 | 5.3526 | 5.5115 | 5.6666 | 5.8181 | 5.9665 | 6.112 | 6.2548 | 6.3952 | 6.5332 | 6.6692 | 6.8032 | 6.9354 | 7.0659 | 7.1949 | 7.4487 | 7.6976 | 7.9422 | 8.1831 | 8.421 | 8.6562 | 8.8892 | 9.1203 | 9.35 | 9.5786
|  | Wmax |  | 11.2396 | m | [8 empty] | 9.7319 | 10.1071 | 10.4828 | 10.86 | 11.2396 | 11.5799 | 11.6568 | 11.7336 | 11.8105 | 11.8874 | 11.9642 | 12.0411 | 12.118 | 12.1949 | 12.2717 | 12.4255 | 12.5792 | 12.7329 | 12.8867 | 13.0404 | 13.1942 | 13.3479 | 13.5016 | 13.6554 | 13.8091
|  | L,W Vsp.min |  | 4.4346 | [9 empty] | 3.9408 | 4.0646 | 4.1853 | 4.303 | 4.4181 | 4.5308 | 4.6413 | 4.7497 | 4.8563 | 4.9611 | 5.0644 | 5.1662 | 5.2666 | 5.3657 | 5.4636 | 5.6564 | 5.8453 | 6.0311 | 6.2141 | 6.3947 | 6.5733 | 6.7502 | 6.9258 | 7.1002 | 7.2737
|  | L,W Vsp.max |  | 8.5351 | [9 empty] | 7.3902 | 7.6751 | 7.9604 | 8.2468 | 8.5351 | 8.8257 | 9.1192 | 9.4162 | 9.7169 | 10.022 | 10.3317 | 10.6465 | 10.9666 | 11.2925 | 11.6244 | 12.3074 | 13.018 | 13.7582 | 14.5299 | 15.3349 | 16.1748 | 17.0513 | 17.9658 | 18.9198 | 19.9146
|  | L,W throw max |  | 9.4595 | [9 empty] | 8.3745 | 8.56 | 8.6183 | 8.6767 | 8.7351 | 8.7935 | 8.8518 | 8.9102 | 8.9686 | 9.027 | 9.0853 | 9.1437 | 9.2021 | 9.2604 | 9.3188 | 9.4356 | 9.5523 | 9.6691 | 9.7858 | 9.9025 | 10.0193 | 10.136 | 10.2528 | 10.3695 | 10.4863
|  | Lmin |  | 4.4346 | m | [8 empty] | 3.9408 | 4.0646 | 4.1853 | 4.303 | 4.4181 | 4.5308 | 4.6413 | 4.7497 | 4.8563 | 4.9611 | 5.0644 | 5.1662 | 5.2666 | 5.3657 | 5.4636 | 5.6564 | 5.8453 | 6.0311 | 6.2141 | 6.3947 | 6.5733 | 6.7502 | 6.9258 | 7.1002 | 7.2737
177 | M | Lmax |  | 8.5351 | m | [8 empty] | 7.3902 | 7.6751 | 7.9604 | 8.2468 | 8.5351 | 8.7935 | 8.8518 | 8.9102 | 8.9686 | 9.027 | 9.0853 | 9.1437 | 9.2021 | 9.2604 | 9.3188 | 9.4356 | 9.5523 | 9.6691 | 9.7858 | 9.9025 | 10.0193 | 10.136 | 10.2528 | 10.3695 | 10.4863
(3-row) | Medium | Wmin |  | 4.4346 | m | [8 empty] | 3.9408 | 4.0646 | 4.1853 | 4.303 | 4.4181 | 4.5308 | 4.6413 | 4.7497 | 4.8563 | 4.9611 | 5.0644 | 5.1662 | 5.2666 | 5.3657 | 5.4636 | 5.6564 | 5.8453 | 6.0311 | 6.2141 | 6.3947 | 6.5733 | 6.7502 | 6.9258 | 7.1002 | 7.2737
|  | Wmax |  | 8.5351 | m | [8 empty] | 7.3902 | 7.6751 | 7.9604 | 8.2468 | 8.5351 | 8.7935 | 8.8518 | 8.9102 | 8.9686 | 9.027 | 9.0853 | 9.1437 | 9.2021 | 9.2604 | 9.3188 | 9.4356 | 9.5523 | 9.6691 | 9.7858 | 9.9025 | 10.0193 | 10.136 | 10.2528 | 10.3695 | 10.4863
|  | L Vsp.min |  | 5.789 | [9 empty] | 5.1443 | 5.306 | 5.4635 | 5.6172 | 5.7674 | 5.9145 | 6.0588 | 6.2003 | 6.3394 | 6.4763 | 6.6111 | 6.7439 | 6.875 | 7.0044 | 7.1322 | 7.3838 | 7.6305 | 7.873 | 8.1118 | 8.3476 | 8.5808 | 8.8117 | 9.0409 | 9.2686 | 9.4951
|  | L Vsp.max |  | 11.1417 | [9 empty] | 9.6471 | 10.019 | 10.3915 | 10.7654 | 11.1417 | 11.5211 | 11.9042 | 12.2918 | 12.6845 | 13.0827 | 13.487 | 13.8979 | 14.3158 | 14.7412 | 15.1744 | 16.0661 | 16.9937 | 17.96 | 18.9674 | 20.0182 | 21.1146 | 22.2588 | 23.4526 | 24.6979 | 25.9965
|  | L throw max |  | 12.3485 | [9 empty] | 10.9321 | 11.1742 | 11.2504 | 11.3266 | 11.4028 | 11.479 | 11.5552 | 11.6314 | 11.7076 | 11.7838 | 11.86 | 11.9362 | 12.0124 | 12.0886 | 12.1648 | 12.3172 | 12.4696 | 12.622 | 12.7744 | 12.9268 | 13.0792 | 13.2316 | 13.384 | 13.5364 | 13.6888
|  | W Vsp.min |  | 3.3548 | [9 empty] | 2.9812 | 3.0748 | 3.1661 | 3.2552 | 3.3423 | 3.4275 | 3.5111 | 3.5931 | 3.6737 | 3.7531 | 3.8312 | 3.9081 | 3.9841 | 4.0591 | 4.1332 | 4.279 | 4.4219 | 4.5624 | 4.7009 | 4.8375 | 4.9726 | 5.1065 | 5.2393 | 5.3712 | 5.5025
|  | W Vsp.max |  | 6.4567 | [9 empty] | 5.5906 | 5.8061 | 6.0219 | 6.2386 | 6.4567 | 6.6766 | 6.8986 | 7.1232 | 7.3508 | 7.5815 | 7.8158 | 8.0539 | 8.2961 | 8.5426 | 8.7937 | 9.3104 | 9.848 | 10.408 | 10.9918 | 11.6007 | 12.2361 | 12.8991 | 13.591 | 14.3126 | 15.0652
|  | W throw max |  | 7.1561 | [9 empty] | 6.3352 | 6.4755 | 6.5197 | 6.5639 | 6.608 | 6.6522 | 6.6963 | 6.7405 | 6.7846 | 6.8288 | 6.873 | 6.9171 | 6.9613 | 7.0054 | 7.0496 | 7.1379 | 7.2262 | 7.3145 | 7.4029 | 7.4912 | 7.5795 | 7.6678 | 7.7561 | 7.8444 | 7.9328
|  | Lmin |  | 5.789 | m | [8 empty] | 5.1443 | 5.306 | 5.4635 | 5.6172 | 5.7674 | 5.9145 | 6.0588 | 6.2003 | 6.3394 | 6.4763 | 6.6111 | 6.7439 | 6.875 | 7.0044 | 7.1322 | 7.3838 | 7.6305 | 7.873 | 8.1118 | 8.3476 | 8.5808 | 8.8117 | 9.0409 | 9.2686 | 9.4951
| L | Lmax |  | 11.1417 | m | [8 empty] | 9.6471 | 10.019 | 10.3915 | 10.7654 | 11.1417 | 11.479 | 11.5552 | 11.6314 | 11.7076 | 11.7838 | 11.86 | 11.9362 | 12.0124 | 12.0886 | 12.1648 | 12.3172 | 12.4696 | 12.622 | 12.7744 | 12.9268 | 13.0792 | 13.2316 | 13.384 | 13.5364 | 13.6888
| Long | Wmin |  | 3.3548 | m | [8 empty] | 2.9812 | 3.0748 | 3.1661 | 3.2552 | 3.3423 | 3.4275 | 3.5111 | 3.5931 | 3.6737 | 3.7531 | 3.8312 | 3.9081 | 3.9841 | 4.0591 | 4.1332 | 4.279 | 4.4219 | 4.5624 | 4.7009 | 4.8375 | 4.9726 | 5.1065 | 5.2393 | 5.3712 | 5.5025
|  | Wmax |  | 6.4567 | m | [8 empty] | 5.5906 | 5.8061 | 6.0219 | 6.2386 | 6.4567 | 6.6522 | 6.6963 | 6.7405 | 6.7846 | 6.8288 | 6.873 | 6.9171 | 6.9613 | 7.0054 | 7.0496 | 7.1379 | 7.2262 | 7.3145 | 7.4029 | 7.4912 | 7.5795 | 7.6678 | 7.7561 | 7.8444 | 7.9328
|  | Pt |  | 4.6693 | Pa | [11 empty] | 4.2075 | 4.6693 | 5.1555 | 5.6662 | 6.2013 | 6.761 | 7.3452 | 7.9539 | 8.5873 | 9.2453 | 9.928 | 10.6354 | 12.1243 | 13.7123 | 15.3996 | 17.1862 | 19.0724 | 21.0583 | 23.1441 | 25.3299 | 27.6159 | 30.0021 | 32.4887 | 35.0759 | 37.7637 | 40.5522 | 43.4416
H.neck | Throw | Lw |  | 19.8877 | dB(A) | [11 empty] | 18.2458 | 19.8877 | 21.4495 | 22.9386 | 24.3615 | 25.7238 | 27.0305 | 28.286 | 29.4941 | 30.6582 | 31.7815 | 32.8666 | 34.9325 | 36.8731 | 38.7028 | 40.4334 | 42.0753 | 43.6371 | 45.1262 | 46.5491 | 47.9115 | 49.2182 | 50.4736 | 51.6817 | 52.8458 | 53.9691 | 55.0543
mm | Setting | Lp* |  | <5 | NC* | [11 empty] | <5 | <5 | 6.4495 | 7.9386 | 9.3615 | 10.7238 | 12.0305 | 13.286 | 14.4941 | 15.6582 | 16.7815 | 17.8666 | 19.9325 | 21.8731 | 23.7028 | 25.4334 | 27.0753 | 28.6371 | 30.1262 | 31.5491 | 32.9115 | 34.2182 | 35.4736 | 36.6817 | 37.8458 | 38.9691 | 40.0543
|  | L Vsp.min |  | 3.3619 | [12 empty] | 3.2751 | 3.3619 | 3.4468 | 3.5298 | 3.6113 | 3.6912 | 3.7697 | 3.8469 | 3.9229 | 3.9977 | 4.0715 | 4.1442 | 4.2871 | 4.4266 | 4.5632 | 4.6973 | 4.829 | 4.9588 | 5.0869 | 5.2133 | 5.3384 | 5.4623 | 5.5852 | 5.7071 | 5.8283 | 5.9489 | 6.0689
|  | L Vsp.max |  | 6.2977 | [12 empty] | 6.1017 | 6.2977 | 6.4938 | 6.6901 | 6.8871 | 7.0851 | 7.2843 | 7.485 | 7.6874 | 7.8918 | 8.0983 | 8.3072 | 8.7328 | 9.1699 | 9.6197 | 10.0836 | 10.5624 | 11.0572 | 11.5689 | 12.0985 | 12.6466 | 13.2141 | 13.8018 | 14.4103 | 15.0404 | 15.6927 | 16.3679
|  | L throw max |  | 5.3863 | [12 empty] | 5.117 | 5.3863 | 5.6556 | 5.9249 | 6.1942 | 6.4635 | 6.7329 | 7.0022 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895
|  | W Vsp.min |  | 5.8251 | [12 empty] | 5.6748 | 5.8251 | 5.9721 | 6.1161 | 6.2571 | 6.3956 | 6.5316 | 6.6654 | 6.797 | 6.9267 | 7.0545 | 7.1806 | 7.4281 | 7.6698 | 7.9065 | 8.1388 | 8.3672 | 8.592 | 8.8139 | 9.033 | 9.2497 | 9.4644 | 9.6773 | 9.8886 | 10.0986 | 10.3074 | 10.5154
|  | W Vsp.max |  | 10.9119 | [12 empty] | 10.5722 | 10.9119 | 11.2516 | 11.5918 | 11.9332 | 12.2762 | 12.6213 | 12.9691 | 13.3198 | 13.6739 | 14.0317 | 14.3937 | 15.131 | 15.8884 | 16.6679 | 17.4715 | 18.3012 | 19.1585 | 20.0452 | 20.9627 | 21.9124 | 22.8958 | 23.914 | 24.9684 | 26.0601 | 27.1904 | 28.3602
|  | W throw max |  | 9.3327 | [12 empty] | 8.866 | 9.3327 | 9.7993 | 10.2659 | 10.7326 | 11.1992 | 11.6658 | 12.1325 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457
|  | Hmin |  | 2.3085 | m | [11 empty] | 2.2931 | 2.3085 | 2.324 | 2.3394 | 2.3548 | 2.3702 | 2.3857 | 2.4011 | 2.4165 | 2.432 | 2.4474 | 2.4628 | 2.4937 | 2.5245 | 2.5554 | 2.5862 | 2.6171 | 2.6479 | 2.6788 | 2.7096 | 2.7405 | 2.7713 | 2.8022 | 2.8331 | 2.8639 | 2.8948 | 2.9256
|  | Lmin |  | 3.3619 | m | [11 empty] | 3.2751 | 3.3619 | 3.4468 | 3.5298 | 3.6113 | 3.6912 | 3.7697 | 3.8469 | 3.9229 | 3.9977 | 4.0715 | 4.1442 | 4.2871 | 4.4266 | 4.5632 | 4.6973 | 4.829 | 4.9588 | 5.0869 | 5.2133 | 5.3384 | 5.4623 | 5.5852 | 5.7071 | 5.8283 | 5.9489 | 6.0689
| S | Lmax |  | 5.3863 | m | [11 empty] | 5.117 | 5.3863 | 5.6556 | 5.9249 | 6.1942 | 6.4635 | 6.7329 | 7.0022 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895 | 7.1895
| Short | Wmin |  | 5.8251 | m | [11 empty] | 5.6748 | 5.8251 | 5.9721 | 6.1161 | 6.2571 | 6.3956 | 6.5316 | 6.6654 | 6.797 | 6.9267 | 7.0545 | 7.1806 | 7.4281 | 7.6698 | 7.9065 | 8.1388 | 8.3672 | 8.592 | 8.8139 | 9.033 | 9.2497 | 9.4644 | 9.6773 | 9.8886 | 10.0986 | 10.3074 | 10.5154
|  | Wmax |  | 9.3327 | m | [11 empty] | 8.866 | 9.3327 | 9.7993 | 10.2659 | 10.7326 | 11.1992 | 11.6658 | 12.1325 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457 | 12.457
|  | L,W Vsp.min |  | 4.4234 | [12 empty] | 4.3093 | 4.4234 | 4.5351 | 4.6444 | 4.7515 | 4.8567 | 4.96 | 5.0615 | 5.1615 | 5.26 | 5.357 | 5.4528 | 5.6407 | 5.8242 | 6.004 | 6.1804 | 6.3538 | 6.5246 | 6.693 | 6.8594 | 7.024 | 7.187 | 7.3487 | 7.5091 | 7.6686 | 7.8272 | 7.9851
|  | L,W Vsp.max |  | 8.2862 | [12 empty] | 8.0283 | 8.2862 | 8.5442 | 8.8025 | 9.0617 | 9.3222 | 9.5843 | 9.8484 | 10.1147 | 10.3836 | 10.6553 | 10.9302 | 11.4901 | 12.0652 | 12.6571 | 13.2674 | 13.8974 | 14.5485 | 15.2218 | 15.9185 | 16.6397 | 17.3864 | 18.1597 | 18.9603 | 19.7894 | 20.6476 | 21.536
|  | L,W throw max |  | 7.087 | [12 empty] | 6.7326 | 7.087 | 7.4413 | 7.7957 | 8.15 | 8.5044 | 8.8587 | 9.2131 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595
|  | Lmin |  | 4.4234 | m | [11 empty] | 4.3093 | 4.4234 | 4.5351 | 4.6444 | 4.7515 | 4.8567 | 4.96 | 5.0615 | 5.1615 | 5.26 | 5.357 | 5.4528 | 5.6407 | 5.8242 | 6.004 | 6.1804 | 6.3538 | 6.5246 | 6.693 | 6.8594 | 7.024 | 7.187 | 7.3487 | 7.5091 | 7.6686 | 7.8272 | 7.9851
216 | M | Lmax |  | 7.087 | m | [11 empty] | 6.7326 | 7.087 | 7.4413 | 7.7957 | 8.15 | 8.5044 | 8.8587 | 9.2131 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595
(4-row) | Medium | Wmin |  | 4.4234 | m | [11 empty] | 4.3093 | 4.4234 | 4.5351 | 4.6444 | 4.7515 | 4.8567 | 4.96 | 5.0615 | 5.1615 | 5.26 | 5.357 | 5.4528 | 5.6407 | 5.8242 | 6.004 | 6.1804 | 6.3538 | 6.5246 | 6.693 | 6.8594 | 7.024 | 7.187 | 7.3487 | 7.5091 | 7.6686 | 7.8272 | 7.9851
|  | Wmax |  | 7.087 | m | [11 empty] | 6.7326 | 7.087 | 7.4413 | 7.7957 | 8.15 | 8.5044 | 8.8587 | 9.2131 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595 | 9.4595
|  | L Vsp.min |  | 5.7743 | [12 empty] | 5.6253 | 5.7743 | 5.9201 | 6.0628 | 6.2026 | 6.3399 | 6.4747 | 6.6073 | 6.7378 | 6.8663 | 6.9931 | 7.118 | 7.3633 | 7.603 | 7.8376 | 8.0679 | 8.2942 | 8.5172 | 8.7371 | 8.9543 | 9.1691 | 9.3819 | 9.5929 | 9.8024 | 10.0106 | 10.2176 | 10.4238
|  | L Vsp.max |  | 10.8168 | [12 empty] | 10.4801 | 10.8168 | 11.1535 | 11.4908 | 11.8292 | 12.1692 | 12.5114 | 12.8561 | 13.2037 | 13.5547 | 13.9095 | 14.2682 | 14.9992 | 15.7499 | 16.5226 | 17.3193 | 18.1417 | 18.9916 | 19.8705 | 20.78 | 21.7215 | 22.6962 | 23.7056 | 24.7508 | 25.8331 | 26.9534 | 28.1131
|  | L throw max |  | 9.2513 | [12 empty] | 8.7888 | 9.2513 | 9.7139 | 10.1765 | 10.639 | 11.1016 | 11.5642 | 12.0267 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485
|  | W Vsp.min |  | 3.3463 | [12 empty] | 3.2599 | 3.3463 | 3.4307 | 3.5134 | 3.5945 | 3.674 | 3.7522 | 3.829 | 3.9046 | 3.9791 | 4.0525 | 4.125 | 4.2671 | 4.406 | 4.542 | 4.6754 | 4.8066 | 4.9358 | 5.0632 | 5.1891 | 5.3136 | 5.4369 | 5.5592 | 5.6806 | 5.8012 | 5.9212 | 6.0407
|  | W Vsp.max |  | 6.2685 | [12 empty] | 6.0733 | 6.2685 | 6.4636 | 6.659 | 6.8551 | 7.0522 | 7.2504 | 7.4502 | 7.6517 | 7.8551 | 8.0606 | 8.2686 | 8.6921 | 9.1272 | 9.575 | 10.0367 | 10.5133 | 11.0058 | 11.5151 | 12.0422 | 12.5878 | 13.1527 | 13.7376 | 14.3433 | 14.9705 | 15.6197 | 16.2917
|  | W throw max |  | 5.3612 | [12 empty] | 5.0932 | 5.3612 | 5.6293 | 5.8974 | 6.1654 | 6.4335 | 6.7015 | 6.9696 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561
|  | Lmin |  | 5.7743 | m | [11 empty] | 5.6253 | 5.7743 | 5.9201 | 6.0628 | 6.2026 | 6.3399 | 6.4747 | 6.6073 | 6.7378 | 6.8663 | 6.9931 | 7.118 | 7.3633 | 7.603 | 7.8376 | 8.0679 | 8.2942 | 8.5172 | 8.7371 | 8.9543 | 9.1691 | 9.3819 | 9.5929 | 9.8024 | 10.0106 | 10.2176 | 10.4238
| L | Lmax |  | 9.2513 | m | [11 empty] | 8.7888 | 9.2513 | 9.7139 | 10.1765 | 10.639 | 11.1016 | 11.5642 | 12.0267 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485 | 12.3485
| Long | Wmin |  | 3.3463 | m | [11 empty] | 3.2599 | 3.3463 | 3.4307 | 3.5134 | 3.5945 | 3.674 | 3.7522 | 3.829 | 3.9046 | 3.9791 | 4.0525 | 4.125 | 4.2671 | 4.406 | 4.542 | 4.6754 | 4.8066 | 4.9358 | 5.0632 | 5.1891 | 5.3136 | 5.4369 | 5.5592 | 5.6806 | 5.8012 | 5.9212 | 6.0407
|  | Wmax |  | 5.3612 | m | [11 empty] | 5.0932 | 5.3612 | 5.6293 | 5.8974 | 6.1654 | 6.4335 | 6.7015 | 6.9696 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561 | 7.1561
[7 empty] | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240 | 250 | 260 | 270 | 280 | 290 | 300 | 320 | 340 | 360 | 380 | 400 | 420 | 440 | 460 | 480 | 500 | 520 | 540 | 560 | 580 | 600